## 2020 Data Set
Index | Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations
|  | Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Notes | EIR Number
1707 | PG&E | 2020-12-27 | 09:18 | 37.7217 | -122.3879 | Other | Urban | 1 meter - < 3 meters | Fire Agency | San Francisco FD | 101812102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-12-27 | 09:18 | Vandalism | N.A. | N.A. | N.A. | Vandalism
1703 | PG&E | 2020-12-22 | 10:13 | 38.0739 | -122.2242 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Vallejo FD | 103163440 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-12-22 | 10:46 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1701 | PG&E | 2020-12-22 | 11:22 | 39.1663083 | -122.1418717 | Vegetation | Agriculture | 1 meter - < 3 meters | Fire Agency | Williams FD | Circuit ID: 062051102 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-12-22 | 11:13 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1692 | PG&E | 2020-12-17 | 09:50 | 35.6958 | -120.2559 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | Customer / Cal Fire | Circuit ID: 182562102 | N | 12000 | Conductor - Primary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
1679 | PG&E | 2020-12-13 | 12:50 | 35.3304 | -119.0094 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Bakersfield FD | Pole ID: 100155808 | Y | 21000 | Insulator | Overhead | Y | 2020-12-13 | 12:48 | Equipment - PG&E | Insulator | N.A. | N.A. | N.A.
1676 | PG&E | 2020-12-12 | 07:47 | 36.4426 | -119.583 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Kings County FD | Pole ID: 100788973 | N | 12000 | Insulator | Overhead | Y | 2020-12-12 | 7:28 | Equipment - PG&E | Insulator | N.A. | N.A. | N.A.
1675 | PG&E | 2020-12-11 | 23:21 | 40.5885483 | -122.2986017 | Other | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103521104; SAP ID: 101464947 | Y | 12000 | Grounding Wire | Overhead | Y | 2020-12-11 | 23:34 | Equipment - PG&E | Grounding Wire | N.A. | N.A. | N.A.
1671 | PG&E | 2020-12-09 | 16:15 | 35.3794 | -119.0972 | Other | Urban | 3 meters - 0.25 Acres | Utility - PG&E | PG&E employee/ Self Extinguished | Circuit Breaker 112 | N | 115000 | Circuit Breaker | Overhead | Y | 2020-12-09 | 16:15 | Equipment - PG&E | Circuit Breaker | N.A. | N.A. | N.A. |  | EI201209A
1663 | PG&E | 2020-12-07 | 11:52 | 35.1536 | -120.6317 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | Cal Fire SLO | Circuit ID: 182631104 | Y | 12000 | Jumper | Overhead | Y | 2020-12-07 | 11:46 | Weather | Jumper | N.A. | N.A. | Weather | High Winds
1662 | PG&E | 2020-12-07 | 10:10 | 37.0705 | -121.9773 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire | Cal Fire Felton | Circuit ID: 083622106, SAP ID: 101799700 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-12-07 | 10:01 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1657 | PG&E | 2020-12-07 | 03:14 | 39.9381717 | -121.7358250 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 102971111, SAP ID: 103357398 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-12-07 | 3:11 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1654 | PG&E | 2020-12-04 | 12:38 | 34.8881 | -120.4241 | Building | Urban | 1 meter - < 3 meters | Self Extinguished | N.A. | Circuit ID: 182061104 | Y | 750 | Conductor - Secondary | Overhead | Y | 2020-12-04 | 12:38 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1653 | PG&E | 2020-12-03 | 19:11 | 35.3472800 | -119.0519067 | Vegetation | Urban | 1 meter - < 3 meters | Customer | N.A. | 253701112 | Y | 750 | Splice/Clamp/Connector | Overhead | N | N.A. | N.A. | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1652 | PG&E | 2020-12-03 | 15:33 | 34.8559 | -120.4512 | Other | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Santa Barbara County FD | 101916205 | Y | 12000 | Jumper | Overhead | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1651 | PG&E | 2020-12-03 | 2:54 | 35.4026317 | -118.9926333 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Bakersfield FD | Circuit ID: 253371101; SAP ID: 100164680; Eqp: Conductor | Y | 12000 | Conductor - Secondary | Overhead | Y | 2020-12-03 | 3:37 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1646 | PG&E | 2020-11-30 | 20:53 | 36.5647 | -121.9118 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 182291101; Between riser 1463 and cutout J-71 | N | 12000 | Conductor - Primary | Underground | Y | 2020-11-30 | 20:53 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1638 | PG&E | 2020-11-30 | 20:47 | 40.3831667 | -122.4516583 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Self Extinguished | N.A. | Meter: 1006281774 | Y | 750 | Service Drop | Overhead | Y | 2020-11-30 | 20:36 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1637 | PG&E | 2020-11-30 | 14:07 | 39.3622500 | -121.8326133 | Other | Agriculture | 10 - 100 Acres | Cal Fire | N.A. | Pole ID: 100377946 | N | 12000 | Pole | Overhead | Y | 2020-11-30 | 8:44 | Contact from object | N.A. | Vehicle | Pole | N.A.
1629 | PG&E | 2020-11-28 | 13:37 | 35.9661 | -121.0914 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | 120106279 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-11-28 | 13:37 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1619 | PG&E | 2020-11-23 | 13:03 | 36.7051 | -121.6556 | Building | Urban | Structure Only | Fire Agency | Salinas FD | N.A. | N.A. | 12000 | N.A. | Overhead | N | N.A. | N.A. | Under Investigation | N.A. | N.A. | N.A. | N.A. | PG&E has included the following ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition. | EI201123A
1614 | PG&E | 2020-11-21 | 17:17 | 37.4875 | -122.2077 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Redwood City FD | 100264583 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-11-21 | 17:17 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
1613 | PG&E | 2020-11-21 | 16:33 | 37.3102517 | -121.8496167 | Other | Urban | 1 meter - < 3 meters | Fire Agency | San Jose FD | Pole ID: 100621989 | Y | 750 | Riser | Overhead | Y | 2020-11-21 | 16:32 | Equipment - PG&E | Riser Failure | N.A. | N.A. | N.A.
1610 | PG&E | 2020-11-20 | 16:45 | 39.9603067 | -122.1882067 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103331102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-11-20 | 16:39 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1731 | PG&E | 2020-11-17 | 10:05 | 35.7181 | -119.5885 | Other | Wetland | 1 meter - < 3 meters | Self Extinguished | N.A. | 100171496 | N | 12000 | Pole | Overhead | Y | 2020-11-17 | 9:51 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A.
1566 | PG&E | 2020-11-17 | 5:55 | 37.3437 | -122.1166 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Santa Clara County FD | Circuit ID: 082161102 | Y | 750 | Conductor - Secondary | Overhead | Y | 2020-11-17 | 5:54 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
1735 | PG&E | 2020-11-13 | 13:18 | 38.2105 | -122.1383 | Building | Urban | Unknown | Self Extinguished | N.A. | 63801102 | N | 12000 | Pothead | Overhead | Y | 2020-11-13 | 13:06 | Equipment - PG&E | Insulator failure | N.A. | N.A. | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
1548 | PG&E | 2020-11-12 | 18:19 | 39.538 | -121.6465867 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103251101 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-11-12 | 18:11 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
1546 | PG&E | 2020-11-12 | 14:51 | 38.3938617 | -122.8707867 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Gold Ridge FD | Circuit ID: 042571101 | Y | 12000 | Service Drop | Overhead | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1545 | PG&E | 2020-11-12 | 08:10 | 38.3928 | -121.5831 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Clarksburg FD | 62462227 | Y | 21000 | Insulator | Overhead | Y | 2020-11-12 | 7:53 | Unknown | Insulator failure | N.A. | N.A. | Unknown | Unknown as to what caused the initial failure, but initial investigation found the ignition to be attributable to PG&E facilities.
1543 | PG&E | 2020-11-11 | 19:22 | 40.4957 | -121.9467 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire | N.A. | 021/108 | N | 500000 | Other | Overhead | N | N.A. | N.A. | Equipment - PG&E | Other | N.A. | N.A. | Other | Induction caused ignition.
1534 | PG&E | 2020-11-10 | 11:34 | 37.3926 | -120.756 | Other | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 252261106 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-11-10 | 11:23 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
1741 | PG&E | 2020-11-10 | 12:36 | 39.2165 | -122.0161 | Other | Urban | Unknown | Unknown | N.A. | 62021101 | Y | 12000 | Jumper | Overhead | N | N.A. | N.A. | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
1527 | PG&E | 2020-11-08 | 17:36 | 38.9909 | -121.4039 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 152811104 | Y | 12000 | Conductor - Primary | Overhead | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1526 | PG&E | 2020-11-08 | 17:06 | 38.2666283 | -122.0026683 | Other | Urban | 3 meters - 0.25 Acres | Utility - PG&E | N.A. | Circuit ID: 063642104 | N | 21000 | Conductor - Primary | Overhead | Y | 2020-11-08 | 17:04 | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
1533 | PG&E | 2020-11-07 | 12:15 | 37.9586 | -122.1974 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | 013/073 | N | 115000 | Jumper | Overhead | Y | 2020-11-07 | 17:50 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
1746 | PG&E | 2020-11-07 | 12:35 | 36.8754 | -120.1012 | Other | Agriculture | Unknown | Unknown | N.A. | 101124349 | N | 12000 | Pole | Overhead | Y | 2020-11-07 | 11:20 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
1508 | PG&E | 2020-11-06 | 10:23 | 36.7295 | -121.279 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | Cal Fire Hollister | Pole ID: 103413616 | N | 21000 | Pole | Overhead | Y | 2020-11-06 | 10:20 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A.
1503 | PG&E | 2020-11-06 | 07:03 | 38.6557 | -121.8673 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Woodland FD | Circuit ID: 063171103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-11-06 | 6:47 | Weather | Conductor failure-all | N.A. | N.A. | Weather | High Winds
1501 | PG&E | 2020-11-05 | 15:28 | 37.2934 | -120.4152 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Merced FD | Pole ID: 101142469 | Y | 12000 | Pole | Overhead | Y | 2020-11-05 | 15:23 | Contact from object | N.A. | Vehicle | Pole | N.A.
1500 | PG&E | 2020-11-05 | 13:59 | 35.2565 | -120.6854 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Fire Agency | SLO FD | Circuit ID: 182951102 | Y | 750 | Conductor - Secondary | Overhead | Y | 2020-11-05 | 13:43 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
1498 | PG&E | 2020-11-04 | 10:42 | 37.1114867 | -119.9890367 | Other | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 254611109 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-11-04 | 11:40 | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
1493 | PG&E | 2020-11-02 | 15:54 | 35.281 | -120.5864 | Other | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Pole ID: 054/303 | N | 115000 | Insulator | Overhead | Y | 2020-11-02 | 15:54 | Contact from object | N.A. | Animal | Insulator | N.A.
1489 | PG&E | 2020-11-02 | 14:15 | 38.2015 | -121.0956 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Clements FD | Circuit ID: 163682102, SAP ID: 102078687 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-11-02 | 14:12 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1488 | PG&E | 2020-11-02 | 12:15 | 34.6817500 | -120.4364967 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Santa Barbara FD | Circuit ID: 183101103, SAP ID: 101913493 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-11-02 | 12:08 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1752 | PG&E | 2020-10-31 | 16:24 | 37.6799 | -121.9057 | Vegetation | Urban | 3 meters - 0.25 Acres | Unknown | N.A. | 100953498 | Unknown | 21000 | Riser | Underground | Y | 2020-10-31 | 16:22 | Equipment - PG&E | Riser Failure | N.A. | N.A. | N.A.
1481 | PG&E | 2020-10-31 | 06:58 | 37.9424 | -122.7011 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Fire Agency | Marin County FD | Ignacio-Bolinas #1 60kV Transmission Circuit between structure 13/145 and 13/144 | N | 60000 | Conductor - Transmission | Overhead | Y | 2020-10-31 | 5:52 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1753 | PG&E | 2020-10-31 | 10:23 | 40.1809 | -122.2554 | Vegetation | Urban | Unknown | Cal Fire | N.A. | Meter: 1008361055 | Y | 750 | Service Drop | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Service Drop | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
1492 | PG&E | 2020-10-30 | 07:07 | 36.2994 | -121.2163 | Vegetation | Barren/Other | 3 meters - 0.25 Acres | Fire Agency | Greenfield FD | Pole ID: 101765306 | N | 21000 | Pole | Overhead | Y | 2020-10-30 | 4:51 | Contact from object | N.A. | Vehicle | Pole | N.A.
1473 | PG&E | 2020-10-30 | 01:50 | 40.6378 | -122.3762 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Redding FD | Pole ID: 101476510 | Y | 12000 | Pole | Overhead | Y | 2020-10-30 | 1:42 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A.
1491 | PG&E | 2020-10-28 | 20:17 | 36.5036 | -121.9315 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Cal Fire | Carmel Highlands and Cypress FPD, Pebble Beach CSD, Monterey Fire Department, and Cal Fire | Circuit ID: 182291102, SAP ID: 101758299 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-28 | 20:15 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1465 | PG&E | 2020-10-27 | 21:28 | 37.898 | -121.7658 | Vegetation | Herbaceous | 0.25 - 10 Acres | Fire Agency | East Contra Costa FD | Pole ID: 100496279 | Y | 21000 | Pole | Overhead | Y | 2020-10-27 | 21:23 | Contact from object | N.A. | Vehicle | Pole | N.A.
1462 | PG&E | 2020-10-27 | 19:45 | 38.584 | -122.6602 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 042711101, SAP ID: 102220160 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-27 | 19:40 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1461 | PG&E | 2020-10-27 | 13:14 | 38.3543 | -121.7495 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Dixon FD | Circuit ID: 062061103 | Y | 750 | Grounding Wire | Overhead | N | N.A. | N.A. | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
1460 | PG&E | 2020-10-27 | 10:41 | 37.2756 | -121.7475 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Agency | San Jose FD | Circuit ID: 083912110 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-10-27 | 10:27 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1711 | PG&E | 2020-10-26 | 6:38 | 37.6607 | -122.4237 | Building | Urban | Structure Only | Fire Agency | South San Francisco | N.A. | Y | 12000 | Service Drop | Overhead | Y | 2020-10-26 | 6:38 | Under Investigation | N.A. | N.A. | N.A. | N.A. | PG&E has included the following ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition. | EI201026B
1458 | PG&E | 2020-10-26 | 14:33 | 38.4336 | -122.9082 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Agency | Graton FD | Pole ID: 102025462 | Y | 12000 | Tie Wire | Overhead | Y | 2020-10-26 | 14:29 | Equipment - PG&E | Tie wire failure | N.A. | N.A. | N.A.
1457 | PG&E | 2020-10-26 | 12:55 | 40.5185 | -124.1631 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | CGC: 113988543957 | Y | 750 | Splice/Clamp/Connector | Overhead | Y | 2020-10-26 | 12:44 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1456 | PG&E | 2020-10-26 | 12:19 | 38.9691 | -121.6206 | Vegetation | Urban | 0.25 - 10 Acres | Fire Agency | The Oswald Tudor FD | Circuit ID: 153711101, SAP ID: 101298559, 101298558 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-26 | 12:00 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1450 | PG&E | 2020-10-26 | 05:05 | 37.2726 | -121.8844 | Building | Urban | 1 meter - < 3 meters | Fire Agency | San Jose FD | Circuit ID: 082311102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-26 | 4:55 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1449 | PG&E | 2020-10-26 | 4:04 | 38.2537283 | -122.0551500 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Fairfield FD | Circuit ID: 062131106, SAP ID: 101659158 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-26 | 3:40 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1447 | PG&E | 2020-10-26 | 3:16 | 38.3659 | -122.8363 | Vegetation | Herbaceous | 0.25 - 10 Acres | Fire Agency | Gold Ridge FD | Circuit ID: 042571104, SAP ID: 101989515 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-26 | 3:11 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1446 | PG&E | 2020-10-26 | 03:16 | 37.4042 | -121.8373 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | San Jose FD | Circuit ID: 083531108 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-26 | 2:59 | Weather | Conductor failure-all | N.A. | N.A. | Weather | High Winds
1445 | PG&E | 2020-10-26 | 00:08 | 38.2605 | -122.0328 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Fairfield FD | Circuit ID: 062131102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-25 | 23:53 | Weather | Conductor failure-all | N.A. | N.A. | Weather | High Winds
1443 | PG&E | 2020-10-25 | 17:31 | 39.5046 | -121.5976 | Vegetation | Urban | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 103251101, SAP ID: 100409439 | Y | 12000 | Conductor - Primary | Overhead | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1453 | PG&E | 2020-10-24 | 14:42 | 38.0103 | -121.6395 | Other | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Contra Costa FD | Pole ID: 103766880 | Y | 21000 | Insulator | Overhead | Y | 2020-10-24 | 11:28 | Equipment - PG&E | Insulator | N.A. | N.A. | N.A.
1436 | PG&E | 2020-10-22 | 21:43 | 38.8809 | -123.6622 | Other | Herbaceous | 1 meter - < 3 meters | Self Extinguished | N.A. | Pole ID: 102187237 | N | 12000 | Fuse | Overhead | N | N.A. | N.A. | Equipment - PG&E | Fuse | N.A. | N.A. | N.A.
1435 | PG&E | 2020-10-22 | 15:23 | 39.2868 | -121.056 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 152481104, SAP Eqp ID: 100077383 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-22 | 15:06 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1433 | PG&E | 2020-10-22 | 15:09 | 34.6002 | -120.192 | Vegetation | Herbaceous | 1 meter - < 3 meters | Customer | N.A. | Pole ID: 101917628 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-10-22 | 15:02 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
1432 | PG&E | 2020-10-22 | 09:02 | 39.5687 | -120.6277 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Agency | Sierra City FD | Pole ID: 103310621 | N | 12000 | Fuse | Overhead | Y | 2020-10-22 | 8:54 | Equipment - PG&E | Fuse failure - all | N.A. | N.A. | N.A.
1430 | PG&E | 2020-10-22 | 09:20 | 40.1498 | -122.2167 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Red Bluff FD | Pole ID: 101537375 | Y | 750 | Grounding Wire | Overhead | N | N.A. | N.A. | Weather | Grounding Wire | N.A. | N.A. | Weather | High Winds
1428 | PG&E | 2020-10-22 | 07:19 | 38.8789 | -121.1178 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire | N.A. | Pole ID: 100045063/ 002/051 | Y | 12000 | Pole | Overhead | Y | 2020-10-22 | 7:06 | Contact from object | N.A. | Vehicle | Pole | N.A.
1427 | PG&E | 2020-10-21 | 15:52 | 38.2067150 | -121.7120917 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Rio Vista FD | Circuit ID: 063642107 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-10-21 | 15:43 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1426 | PG&E | 2020-10-21 | 14:50 | 38.1585300 | -121.6917867 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Rio Vista FD | Circuit ID: 062462225 | Y | 12000 | Service Drop | Overhead | Y | 2020-10-21 | 14:32 | Contact from object | N.A. | Vegetation | Service Drop | N.A.
1422 | PG&E | 2020-10-20 | 00:02 | 39.1013 | -121.5804 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | Olivehurst FD | Circuit ID: 152901101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-20 | 23:53 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1421 | PG&E | 2020-10-19 | 15:23 | 35.5971683 | -120.6578600 | Other | Barren/Other | 3 meters - 0.25 Acres | Fire Agency | Paso Robles FD | Circuit ID: 182611106, SAP: 41121346 | Y | 21000 | Jumper | Overhead | Y | 2020-10-19 | 15:21 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
1412 | PG&E | 2020-10-18 | 19:39 | 37.8462 | -120.897 | Other | Herbaceous | 3 meters - 0.25 Acres | Customer | N.A. | Pole ID: 103151988 | N | 750 | Riser | Overhead | Y | 2020-10-18 | 19:21 | Equipment - PG&E | Riser Failure | N.A. | N.A. | N.A.
1407 | PG&E | 2020-10-18 | 13:10 | 38.9155050 | -121.3465217 | Other | Herbaceous | 0.25 - 10 Acres | Fire Agency | Lincoln FD | Pole ID: 100089743 | N | 12000 | Lightning Arrestor | Overhead | Y | 2020-10-18 | 12:20 | Contact from object | N.A. | Animal | Lightning Arrestor | N.A.
1398 | PG&E | 2020-10-17 | 13:27 | 38.4204 | -122.9548 | Building | Hardwood Forest | 1 meter - < 3 meters | Cal Fire | N.A. | N.A. | N.A. | 12000 | N.A. | Overhead | N | N.A. | N.A. | Under Investigation | N.A. | N.A. | N.A. | N.A. | PG&E has included the following ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition. | EI201017A
1401 | PG&E | 2020-10-17 | 15:10 | 36.7264 | -119.7678 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Fresno FD | Meter: 1010546607 | Y | 750 | Service Drop | Overhead | Y | 2020-10-17 | 15:10 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1391 | PG&E | 2020-10-16 | 11:01 | 36.9566 | -121.727 | Other | Urban | 3 meters - 0.25 Acres | Customer | N.A. | LR: 135762 | Y | 21000 | Recloser | Overhead | Y | 2020-10-16 | 11:01 | Contact from object | N.A. | Animal | Recloser | N.A.
1389 | PG&E | 2020-10-16 | 04:23 | 38.4113 | -122.9801 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 042571102, SAP: 101974096 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-16 | 4:13 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1418 | PG&E | 2020-10-15 | 19:39 | 39.0272 | -121.8666 | Vegetation | Agriculture | 0.25 - 10 Acres | Fire Agency | Colusa FD | Pole ID: 103689220 | N | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-10-15 | 19:34 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1415 | PG&E | 2020-10-15 | 07:08 | 40.3236 | -122.4294 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 101511399, SAP Eqp ID: 101511399 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-15 | 7:02 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
1381 | PG&E | 2020-10-15 | 12:44 | 40.3614283 | -122.3492700 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 102931101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-15 | 13:56 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1380 | PG&E | 2020-10-15 | 13:01 | 40.5943 | -122.2387 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103351104 | N | 750 | Service Drop | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Service Drop | N.A.
1375 | PG&E | 2020-10-14 | 19:22 | 38.8072617 | -121.2052067 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Rocklin FD | Pole ID: 100058463 | N | 12000 | Pole | Overhead | Y | 2020-10-14 | 20:00 | Contact from object | N.A. | Vehicle | Pole | N.A.
1374 | PG&E | 2020-10-14 | 18:45 | 39.6773 | -121.8439 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire | N.A. | 103081107 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-14 | 18:45 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1370 | PG&E | 2020-10-13 | 16:21 | 35.5542 | -119.8054 | Other | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | 252321103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-13 | 16:21 | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
1369 | PG&E | 2020-10-13 | 14:34 | 38.0344 | -121.6507 | Other | Herbaceous | 1 meter - < 3 meters | Fire Agency | Contra Costa FD | Circuit ID: 014592112 Pole ID: 100457182 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-10-13 | 14:27 | Equipment - PG&E | Insulator failure | N.A. | N.A. | N.A.
1366 | PG&E | 2020-10-13 | 00:02 | 37.8029 | -122.2789 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | Oakland FD | Circuit ID: 012011113 | Y | 750 | Service Drop | Overhead | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1364 | PG&E | 2020-10-12 | 00:05 | 40.5136 | -124.1282 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Rio Dell FD | Circuit ID: 192251101, between Pole ID: 100998306 and 103168487 | N | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-10-11 | 23:57 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1363 | PG&E | 2020-10-11 | 23:29 | 37.0217 | -120.0712 | Vegetation | Urban | 1 meter - < 3 meters | Cal Fire | N.A. | 254611111 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-11 | 23:29 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1361 | PG&E | 2020-10-10 | 01:13 | 35.3873 | -118.9393 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Bakersfield FD | Circuit ID: 253951109, SAP ID: 102296159 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-10 | 1:11 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1356 | PG&E | 2020-10-07 | 13:08 | 39.1488650 | -122.2519667 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Williams FD | Circuit ID: 062051102 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-10-07 | 12:49 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
1353 | PG&E | 2020-10-05 | 14:44 | 38.1167 | -120.8907 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | Cal Fire and Calaveras Consolidated Fire | Circuit ID: 162991102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-05 | 14:40 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
1341 | PG&E | 2020-10-04 | 16:23 | 38.7308483 | -121.1934033 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Granite Bay FD | Circuit ID: 152571105, SAP ID: 100066291 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-04 | 16:18 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1340 | PG&E | 2020-10-04 | 16:23 | 35.6299 | -120.3603 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Self Extinguished | N.A. | Circuit ID: 182562102 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-10-04 | 16:04 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1335 | PG&E | 2020-10-03 | 16:47 | 38.5054 | -122.8392 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Sonoma County FD | Circuit ID: 042561102, SAP ID: 103593452 | Y | 12000 | Conductor - Secondary | Overhead | Y | 2020-10-03 | 17:46 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
1334 | PG&E | 2020-10-03 | 15:29 | 37.4889 | -122.2065 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Redwood City FD | Circuit ID: 024161102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-03 | 14:33 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
1332 | PG&E | 2020-10-02 | 20:10 | 37.2524683 | -120.3159017 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 255361112, SAP ID: 101082275 | Y | 12000 | Service Drop | Overhead | Y | 2020-10-02 | 21:06 | Contact from object | N.A. | Vegetation | Service Drop | N.A.
1330 | PG&E | 2020-10-02 | 15:45 | 39.133 | -121.0792 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 152691103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-02 | 15:21 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1329 | PG&E | 2020-10-02 | 15:12 | 38.468 | -121.9369 | Vegetation | Urban | 1 meter - < 3 meters | Customer | N.A. | Circuit ID: 063591103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-02 | 15:02 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1324 | PG&E | 2020-10-01 | 12:05 | 37.0045 | -120.0835 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 254611111 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-10-01 | 12:05 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A. |  | EI201001A
1318 | PG&E | 2020-09-29 | 16:22 | 38.2455 | -121.7618 | Vegetation | Herbaceous | 1 meter - < 3 meters | Customer | N.A. | Pole ID: 101582151 | Y | 12000 | Pole | Overhead | Y | 2020-09-29 | 16:36 | Contact from object | N.A. | Vehicle | Pole | N.A.
1314 | PG&E | 2020-09-29 | 01:40 | 38.8368 | -122.0291 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Utility - PG&E | N.A. | Circuit ID: 102841102 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-09-29 | 1:22 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1310 | PG&E | 2020-09-28 | 18:21 | 37.9652 | -122.1388 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Customer | N.A. | 1006560423 | Y | 12000 | Service Drop | Overhead | Y | 2020-09-28 | 18:19 | Unknown | Conductor failure-all | N.A. | N.A. | Unknown | Unknown as to what caused the initial failure, but initial investigation found the ignition to be attributable to PG&E facilities.
1623 | PG&E | 2020-09-28 | 15:51 | 39.6531 | -121.4494 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103751102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-28 | 15:45 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1309 | PG&E | 2020-09-28 | 13:35 | 37.958 | -122.2736 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Richmond FD | 14341106 | Y | 12000 | Conductor - Insulated Secondary | Overhead | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1308 | PG&E | 2020-09-28 | 8:57 | 37.5292 | -121.99 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Fremont FD | Pole ID: 100946344 | Y | 12000 | Pole | Overhead | Y | 2020-09-28 | 8:40 | Contact from object | N.A. | Vehicle | Pole | N.A.
1368 | PG&E | 2020-09-27 | 14:48 | 40.5392 | -122.5666 | Vegetation | Hardwood Forest | 100 + Acres | Cal Fire | N.A. | N.A. | N.A. | 12000 | N.A. | Overhead | Y | 2020-09-27 | 14:48 | Under Investigation | N.A. | N.A. | N.A. | N.A. | PG&E has included the Zogg Fire in this ignition report because CAL FIRE has announced that the cause of the Zogg Fire was a pine tree contacting PG&E overhead electric lines. PG&E's investigation into the cause of the Zogg Fire is ongoing. | EI200927A
1304 | PG&E | 2020-09-27 | 19:32 | 38.2736 | -122.5761 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Petaluma FD | Circuit ID: 043371102 between Pole ID: 101990098 and 102005005 | Y | 12000 | Automatic Wire Splice | Overhead | Y | 2020-09-27 | 19:24 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1300 | PG&E | 2020-09-27 | 16:56 | 37.7884817 | -121.7699533 | Vegetation | Urban | 0.25 - 10 Acres | Fire Agency | San Ramon FD | Circuit ID: 014422109, Fuse: 71415 | Y | 21000 | Fuse | Overhead | Y | 2020-09-27 | 16:24 | Equipment - PG&E | Fuse failure - all | N.A. | N.A. | N.A.
1297 | PG&E | 2020-09-27 | 15:30 | 40.4491500 | -122.3089300 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Anderson FD | Circuit ID: 103261101, SAP ID: 101496897 | Y | 12000 | Service Drop | Overhead | Y | 2020-09-27 | 15:27 | Contact from object | N.A. | Vegetation | Service Drop | N.A.
1295 | PG&E | 2020-09-27 | 08:11 | 37.9970867 | -123.0156333 | Vegetation | Shrub | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit 042291101 Pole ID:102246615 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-27 | 9:13 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1764 | PG&E | 2020-09-26 | 20:17 | 39.1281 | -121.6392 | Vegetation | Urban | Unknown | Fire Agency | Yuba City Fire dept | 101300049 | Y | 12000 | Insulator | Overhead | N | N.A. | N.A. | Equipment - PG&E | Insulator failure | N.A. | N.A. | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
1288 | PG&E | 2020-09-24 | 15:44 | 39.2652567 | -121.5293633 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103211102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-24 | 16:01 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
1284 | PG&E | 2020-09-23 | 15:31 | 38.2262883 | -122.5311867 | Vegetation | Herbaceous | 10 - 100 Acres | Cal Fire | N.A. | Pole ID: 103999142 | Y | 12000 | Pole | Overhead | Y | 2020-09-23 | 15:23 | Contact from object | N.A. | Vehicle | Pole | N.A.
1283 | PG&E | 2020-09-23 | 12:17 | 37.6869067 | -122.1469900 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Alco FD | Circuit ID: 013111110 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-23 | 12:02 | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
1282 | PG&E | 2020-09-23 | 10:26 | 36.8185 | -121.4507 | Vegetation | Herbaceous | 10 - 100 Acres | Cal Fire | N.A. | Circuit ID: 182742101 | N | 21000 | Conductor - Primary | Overhead | Y | 2020-09-23 | 23:31 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
1279 | PG&E | 2020-09-22 | 10:32 | 38.0965 | -121.5214 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Customer | N.A. | Circuit ID: 062462224 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-09-22 | 7:44 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1276 | PG&E | 2020-09-21 | 19:51 | 38.6063 | -121.0226 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 153612103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-21 | 19:40 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1766 | PG&E | 2020-09-21 | 12:05 | 39.4685 | -121.5775 | Building | Urban | Unknown | Self Extinguished | N.A. | 100359938 | Y | 12000 | Pole | Overhead | Y | 2020-09-21 | 11:56 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
1274 | PG&E | 2020-09-20 | 11:50 | 36.5333883 | -121.4238217 | Vegetation | Barren/Other | 3 meters - 0.25 Acres | Fire Agency | Gonzales FD | Circuit ID: 182131101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-20 | 11:46 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1271 | PG&E | 2020-09-18 | 21:52 | 34.4132 | -119.0811 | Vegetation | Shrub | 3 meters - 0.25 Acres | Fire Agency | Kern County FD | Circuit ID: 253391106 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-18 | 21:50 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1270 | PG&E | 2020-09-18 | 17:49 | 38.7188 | -121.7841 | Vegetation | Agriculture | 1 meter - < 3 meters | Fire Agency | Willow Creek FD | Circuit ID: 063191105 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-18 | 16:38 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1268 | PG&E | 2020-09-18 | 15:20 | 38.4263450 | -122.6845133 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Fire Agency | Santa Rosa FD | Circuit ID: 042151111 | Y | 750 | Conductor - Secondary | Overhead | Y | 2020-09-18 | 15:52 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
1265 | PG&E | 2020-09-17 | 14:19 | 36.5551 | -119.2422 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Tulare County FD | Pole ID: 100725983 | N | 12000 | Guy/Span Wire | Overhead | Y | 2020-09-17 | 13:58 | Contact from object | N.A. | Vehicle | Guy/Span Wire | N.A.
1263 | PG&E | 2020-09-17 | 08:54 | 38.8338 | -121.1894 | Other | Urban | 1 meter - < 3 meters | Unknown | N.A. | 3423 | N | 12000 | Pothead | Overhead | Y | 2020-09-17 | 8:47 | Contact from object | N.A. | Animal | Pothead | N.A.
1258 | PG&E | 2020-09-16 | 16:47 | 37.691 | -122.4126 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire | Cal Fire/Brisbane FD | Switch: 2849 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-09-16 | 16:35 | Equipment - PG&E | Fuse failure - all | N.A. | N.A. | N.A.
1253 | PG&E | 2020-09-14 | 06:11 | 36.0177 | -119.4737 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | 046/346 | N | 115000 | Conductor - Transmission | Overhead | Y | 2020-09-14 | 6:02 | Contact from object | N.A. | Animal | Conductor - Transmission | N.A.
1244 | PG&E | 2020-09-12 | 14:29 | 37.8796667 | -120.4571033 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 163781701 | N | 17000 | Conductor - Secondary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vehicle | Conductor - Secondary | N.A.
1238 | PG&E | 2020-09-11 | 10:34 | 38.9564 | -121.1062 | Other | Hardwood Woodland | 1 meter - < 3 meters | Fire Agency | Auburn FD | Fuse: 9953 | Y | 12000 | Fuse | Overhead | Y | 2020-09-11 | 10:24 | Contact from object | N.A. | Animal | Fuse | N.A.
1225 | PG&E | 2020-09-09 | 10:48 | 38.1685 | -120.3913 | Vegetation | Shrub | 0.25 - 10 Acres | Cal Fire | N.A. | Eqp ID: 79826 | N | 17000 | Recloser | Padmounted | Y | 2020-09-09 | 10:53 | Equipment - PG&E | Recloser failure | N.A. | N.A. | N.A.
1219 | PG&E | 2020-09-08 | 22:02 | 40.0182 | -122.0876 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103481102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-08 20:55 | 20:55 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1216 | PG&E | 2020-09-08 | 18:18 | 38.4479 | -121.8583 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Dixon FD | Circuit ID: 062061106 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-08 18:12 | 18:12 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
1209 | PG&E | 2020-09-08 | 14:41 | 37.6535 | -121.6739 | Other | Agriculture | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 013751102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-08 14:30 | 14:30 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1204 | PG&E | 2020-09-08 | 11:21 | 40.4374 | -122.2991 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Anderson FD | Circuit ID: 103261101 | Y | 12000 | Conductor - Secondary | Overhead | Y | 2020-09-08 | 11:20 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
1200 | PG&E | 2020-09-08 | 03:06 | 40.1865 | -122.2141 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 103531103, SAP Eqp ID: 101544948 | Y | 12000 | Pole | Overhead | Y | 2020-09-08 03:39 | 3:39 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
1199 | PG&E | 2020-09-08 | 02:33 | 40.4684 | -122.3114 | Vegetation | Urban | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103441102, SAP ID: 101496111, 101496112 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-08 01:45 | 1:45 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1281 | PG&E | 2020-09-07 | 04:26 | 37.9487 | -122.5201 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Central Marin FD | Meter: 1007683605 | Y | 750 | Service Drop | Overhead | Y | 2020-09-07 | 04:26 | Contact from object | N.A. | Vegetation | Service Drop | N.A.
1197 | PG&E | 2020-09-07 | 18:04 | 37.0008 | -121.8851 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Fire Agency | Rio Del Mar FD | Circuit ID: 083692105 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-09-07 18:30 | 18:30 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1195 | PG&E | 2020-09-07 | 16:18 | 38.831 | -123.0471 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 042821101, SAP ID: 101964553 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-07 | 16:14 | Contact from object | N.A. | Other | Conductor - Primary | Weather | Communication line making contact with Primary
1193 | PG&E | 2020-09-07 | 11:27 | 36.5459 | -121.3914033 | Other | Herbaceous | 0.25 - 10 Acres | Fire Agency | Gonzales FD | Structure: 018/093; SAP Eqp: 40650909 | N | 115000 | Conductor - Transmission | Overhead | Y | 2020-09-07 | 10:58 | Contact from object | N.A. | Animal | Conductor - Transmission | N.A.
1190 | PG&E | 2020-09-06 | 20:58 | 37.0174 | -122.1224 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Cal Fire | Cal Fire & Scotts Valley FD | Circuit ID: 083252107 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-09-06 17:07 | 17:07 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
1185 | PG&E | 2020-09-06 | 16:47 | 36.8737 | -121.5854 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire | N.A. | CGC: 412443857077 | Y | 12000 | Transformer | Overhead | Y | 2020-09-06 16:39 | 16:39 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
1184 | PG&E | 2020-09-06 | 14:29 | 41.2493 | -123.7669 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 192401101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-06 14:27 | 14:27 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1183 | PG&E | 2020-09-06 | 13:09 | 37.7977 | -121.4548 | Other | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Tracy FD | Circuit ID: 162881106 | Y | 12000 | Conductor - Primary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
1182 | PG&E | 2020-09-06 | 13:04 | 38.9551 | -123.5911 | Other | Conifer Forest | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 043381101 | Y | 12000 | Service Drop | Overhead | N | N.A. | N.A. | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
1181 | PG&E | 2020-09-06 | 12:49 | 34.6026 | -120.1462 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Santa Barbara County FD | Circuit ID: 183041102 | Y | 12000 | Conductor - Open Wire Secondary | Overhead | Y | 2020-09-06 12:46 | 12:46 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1180 | PG&E | 2020-09-06 | 09:00 | 35.5055 | -119.6895 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Kern County FD | Pole ID: 100238348 | Y | 12000 | Pole | Overhead | Y | 2020-09-06 08:41 | 8:41 | Contact from object | N.A. | Vehicle | Pole | N.A.
1178 | PG&E | 2020-09-05 | 20:57 | 40.1129 | -123.7498 | Other | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | 44913382 | N | 60000 | Conductor - Transmission | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Animal | Conductor - Transmission | N.A.
1176 | PG&E | 2020-09-05 | 15:37 | 39.2003 | -120.8383 | Other | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | N.A. | 1327 | N | 12000 | Switch | Overhead | N | N.A. | N.A. | Equipment - PG&E | Switch failure | N.A. | N.A. | N.A.
1174 | PG&E | 2020-09-05 | 7:50 | 37.2362 | -121.9364 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Agency | Santa Clara County FD | Circuit ID: 083431116, SAP ID: 100516737 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-05 | 7:44 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
1173 | PG&E | 2020-09-05 | 07:59 | 36.5866 | -121.6016 | Other | Urban | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 182731102 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-09-05 07:38 | 7:38 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1171 | PG&E | 2020-09-04 | 15:21 | 37.4879 | -122.2119 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Redwood City FD | Circuit ID: 024161102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-04 | 15:20 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1168 | PG&E | 2020-09-03 | 13:01 | 34.6665 | -120.1328 | Other | Herbaceous | 0.25 - 10 Acres | Fire Agency | Santa Barbara County FD | Circuit ID: 182721104 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-09-03 14:21 | 12:45 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A.
1159 | PG&E | 2020-09-01 | 12:04 | 34.8976 | -120.2976 | Vegetation | Agriculture | 1 meter - < 3 meters | Customer | N.A. | CGC: 513113551650 | N | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-09-01 13:16 | 13:16 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1158 | PG&E | 2020-09-01 | 11:15 | 39.4085 | -121.29 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 103201102 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-09-01 10:15 | 10:15 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1154 | PG&E | 2020-08-31 | 10:28 | 38.6414 | -121.5895 | Other | Agriculture | 3 meters - 0.25 Acres | Fire Agency | West Sacramento FD | Capacitor Bank: C497 | Y | 12000 | Capacitor Bank | Overhead | N | N.A. | N.A. | Equipment - PG&E | Capacitor bank failure | N.A. | N.A. | N.A.
1151 | PG&E | 2020-08-30 | 23:50 | 37.6878 | -121.4162 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Tracy FD | Circuit ID: 163091101; SAP ID: 102054685 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-30 00:10 | 22:40 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1149 | PG&E | 2020-08-30 | 13:30 | 36.7818 | -119.8113 | Vegetation | Urban | 1 meter - < 3 meters | Unknown | N.A. | Meter: 1004234040 | Y | 750 | Service Drop | Overhead | Y | 2020-08-30 14:29 | 14:29 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1148 | PG&E | 2020-08-30 | 13:24 | 39.486 | -121.5062 | Vegetation | Urban | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 102911107, SAP ID: 100395767 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-30 13:17 | 13:17 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1139 | PG&E | 2020-08-26 | 13:23 | 39.5638 | -123.4024 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Cal Fire | Cal Fire Mendocino Unit | Circuit ID: 042681102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-26 | 13:19 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1135 | PG&E | 2020-08-26 | 16:05 | 38.1131 | -121.403 | Other | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Woodbridge FD | Fuse: 3783 | Y | 21000 | Fuse | Overhead | Y | 2020-08-26 15:11 | 15:11 | Equipment - PG&E | Fuse failure - all | N.A. | N.A. | N.A.
1141 | PG&E | 2020-08-25 | 07:50 | 37.9186 | -122.5548 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished | N.A. | Fuse: 2443 | Y | 12000 | Fuse | Overhead | Y | 2020-08-25 06:15 | 6:15 | Equipment - PG&E | Fuse failure - all | N.A. | N.A. | N.A.
1131 | PG&E | 2020-08-25 | 20:47 | 38.8461 | -121.3958 | Other | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 152442110 | Y | 21000 | Jumper | Overhead | Y | 2020-08-25 | 20:46 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
1130 | PG&E | 2020-08-25 | 18:00 | 38.8461 | -121.3776 | Other | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 152442110 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-08-25 | 15:30 | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
1129 | PG&E | 2020-08-25 | 17:32 | 38.8374883 | -121.3957267 | Other | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 152442110 | N | 12000 | Jumper | Overhead | Y | 2020-08-25 | 22:17 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
1125 | PG&E | 2020-08-25 | 16:25 | 38.7389 | -121.1936 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | South Placer FD | Circuit ID: 152571102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-25 16:18 | 16:18 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1120 | PG&E | 2020-08-25 | 08:47 | 40.2776 | -122.3078 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown | N.A. | CGC: 119145034420 | N | 12000 | Transformer | Overhead | Y | 2020-08-25 | 8:43 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
1605 | PG&E | 2020-08-24 | 17:38 | 38.5657 | -122.5752 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 042711102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-24 | 17:34 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1115 | PG&E | 2020-08-23 | 06:46 | 36.8946 | -121.8152 | Vegetation | Agriculture | 1 meter - < 3 meters | Fire Agency | Pajaro Dunes FD | Circuit ID: 083192103 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-08-23 06:45 | 6:45 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1113 | PG&E | 2020-08-23 | 02:02 | 36.6844 | -120.2603 | Other | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Fresno County Fire Prevention | Circuit ID: 252361112 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-22 23:49 | 23:49 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1106 | PG&E | 2020-08-21 | 16:35 | 40.602 | -122.2494 | Other | Urban | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 103351104 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-21 11:31 | 11:31 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
1104 | PG&E | 2020-08-21 | 15:45 | 38.7222 | -120.8101 | Other | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit: El Dorado-Missouri Flats #1, Structure: 13/115 | N | 12000 | Insulator | Overhead | Y | 2020-08-21 | 15:21 | Equipment - PG&E | Insulator failure | N.A. | N.A. | N.A.
1103 | PG&E | 2020-08-21 | 15:24 | 37.707 | -121.644 | Other | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Alco FD | Circuit ID: 013751103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-21 15:10 | 15:10 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
1094 | PG&E | 2020-08-20 | 19:23 | 40.1536 | -122.238 | Vegetation | Urban | 0.25 - 10 Acres | Fire Agency | Red Bluff FD | Pole ID: 101536445/A022/175 | Y | 12000 | Pole | Overhead | Y | 2020-08-20 | 19:16 | Contact from object | N.A. | Vehicle | Pole | N.A.
1087 | PG&E | 2020-08-20 | 11:47 | 38.9324 | -122.7515 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Unknown | Third-Party | Circuit ID: 043311102 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-08-20 11:03 | 11:40 | Contact from object | N.A. | Other | Conductor - Primary | Human Error | Third party excavator boom making contact with transmission line.
1081 | PG&E | 2020-08-20 | 01:49 | 36.2388 | -120.3015 | Other | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 252381107 Pole ID: 100743822 | Y | 12000 | Insulator | Overhead | Y | 2020-08-20 00:51 | 0:51 | Contact from object | N.A. | Animal | Insulator | N.A.
1077 | PG&E | 2020-08-20 | 00:42 | 39.0046 | -122.8941 | Other | Agriculture | 1 meter - < 3 meters | Unknown | N.A. | Circuit ID: 042141101, SAP ID: 102159653 | Y | 12000 | Transformer | Overhead | Y | 2020-08-20 00:19 | 0:19 | Weather | Transformer failure | N.A. | N.A. | Weather | Lightning
1604 | PG&E | 2020-08-19 | 04:41 | 39.0892 | -121.1163 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 152691109 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-19 | 4:01 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1095 | PG&E | 2020-08-19 | 09:19 | 39.137 | -121.0175 | Other | Hardwood Woodland | 1 meter - < 3 meters | Unknown | N.A. | Circuit: Drum-Rio Oso #2; Structure: 16/135 | N | 115000 | Conductor - Transmission | Overhead | Y | 2020-08-19 | 09:19 | Contact from object | N.A. | Animal | Conductor - Transmission | N.A.
1072 | PG&E | 2020-08-19 | 14:31 | 38.795 | -121.2336 | Other | Urban | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 152061104 | Y | 12000 | Service Drop | Overhead | Y | 2020-08-19 | 14:21 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
1069 | PG&E | 2020-08-19 | 6:45 | 39.4145 | -123.7815 | Other | Conifer Forest | 3 meters - 0.25 Acres | Customer | N.A. | Circuit ID: 042761102 | Y | 12000 | Conductor - Secondary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
1068 | PG&E | 2020-08-19 | 06:41 | 38.8362 | -120.9515 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 153652109 | N | 21000 | Conductor - Primary | Overhead | Y | 2020-08-19 06:22 | 6:22 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1059 | PG&E | 2020-08-18 | 18:24 | 37.9752 | -121.3248 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Stockton FD | Circuit: 163121106 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-08-18 | 18:23 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1057 | PG&E | 2020-08-18 | 14:58 | 37.5963 | -121.6364 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | PG&E SIPT / Cal Fire | Circuit ID: 013751102 | Y | 750 | Conductor - Secondary | Overhead | Y | 2020-08-18 | 14:56 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A. |  | EI200818B
1056 | PG&E | 2020-08-18 | 11:00 | 39.2125 | -121.4788 | Other | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Browns Valley FD | Circuit ID: 152331108, SAP ID: 41154781 | Y | 12000 | Capacitor Bank | Overhead | Y | 2020-08-18 | 10:59 | Weather | Capacitor bank failure | N.A. | N.A. | Weather | Lightning
1090 | PG&E | 2020-08-17 | 05:49 | 39.3305 | -121.1959 | Other | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | Cal Fire NEU West | Circuit: Colgate-Palermo; Structure: 000/008 | N | 60000 | Insulator | Overhead | Y | 2020-08-17 | 5:49 | Weather | Insulator | N.A. | N.A. | Weather | Lightning
1089 | PG&E | 2020-08-17 | 18:11 | 38.8151 | -120.8734 | Vegetation | Hardwood Forest | 10 - 100 Acres | Cal Fire | N.A. | Circuit ID: 153082106 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-08-17 17:55 | 17:55 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1051 | PG&E | 2020-08-17 | 20:11 | 37.8566 | -122.0729 | Other | Urban | 3 meters - 0.25 Acres | Cal Fire | N.A. | CGC: 315462149780 | N | 12000 | Transformer | Underground | Y | 2020-08-17 | 21:07 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
1050 | PG&E | 2020-08-17 | 18:18 | 38.8877 | -122.5852 | Other | Urban | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 043361103, SAP ID: 103941864 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-08-17 | 18:18 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1045 | PG&E | 2020-08-17 | 02:12 | 38.9278 | -121.3578 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Lincoln FD | Fuse: 7315 | Y | 12000 | Fuse | Overhead | Y | 2020-08-17 | 1:40 | Weather | Fuse | N.A. | N.A. | Weather | Lightning
1042 | PG&E | 2020-08-16 | 16:49 | 37.1734 | -122.0628 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Agency | Cupertino FD | Circuit ID: 082021106 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-16 03:00 | 3:00 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1039 | PG&E | 2020-08-16 | 15:27 | 37.5239 | -122.3534 | Vegetation | Urban | 0.25 - 10 Acres | Fire Agency | San Mateo County FD | Pole ID: 100257344 | N | 12000 | Insulator | Overhead | Y | 2020-08-16 15:10 | 15:10 | Equipment - PG&E | Insulator failure | N.A. | N.A. | N.A.
1037 | PG&E | 2020-08-16 | 15:25 | 37.2493 | -122.0316 | Vegetation | Urban | 0.25 - 10 Acres | Fire Agency | Santa Clara County FD | Circuit ID: 083371107 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-16 14:57 | 14:57 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1036 | PG&E | 2020-08-16 | 12:32 | 37.2542 | -121.9144 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | San Jose FD | Circuit ID: 083431109 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-08-16 | 12:22 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1032 | PG&E | 2020-08-16 | 07:46 | 37.1663 | -121.9918 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 082021106 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-16 02:54 | 2:51 | Weather | Conductor - Primary | N.A. | N.A. | Weather | Lightning
1031 | PG&E | 2020-08-16 | 07:33 | 38.4233 | -121.9533 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Vacaville FD | Circuit ID: 063591105 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-16 07:28 | 7:28 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1044 | PG&E | 2020-08-15 | 15:55 | 37.322 | -121.996 | Vegetation | Urban | 0.25 - 10 Acres | Fire Agency | San Jose FD | Pole ID:100535290 | N | 12000 | Guy/Span Wire | Overhead | Y | 2020-08-15 15:47 | 15:47 | Contact from object | N.A. | Vegetation | Guy/Span Wire | N.A. |  | EI200815A
1025 | PG&E | 2020-08-15 | 20:48 | 40.1121 | -122.1602 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 103391102, SAP ID: 101543506 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-15 20:42 | 20:43 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1024 | PG&E | 2020-08-15 | 18:31 | 38.2596 | -122.0753 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Fairfield FD | CGC: 219786921602 | N | 12000 | Transformer | Underground | Y | 2020-08-15 17:56 | 17:56 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
1023 | PG&E | 2020-08-15 | 18:22 | 37.6959 | -121.4327 | Other | Urban | 0.25 - 10 Acres | Fire Agency | South County FD | Circuit ID: 163091102, SAP ID: 102053187 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-15 18:14 | 18:14 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1022 | PG&E | 2020-08-15 | 17:50 | 37.4189 | -121.9113 | Vegetation | Urban | 0.25 - 10 Acres | Fire Agency | Milpitas FD | Circuit ID: 083892108, SAP ID: 100558631 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-08-15 17:42 | 17:42 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
1021 | PG&E | 2020-08-15 | 17:26 | 39.3721 | -121.7114 | Vegetation | Urban | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 103241101, SAP ID: 100377121 | Y | 12000 | Conductor - Secondary | Overhead | Y | 2020-08-15 | 17:25 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
1017 | PG&E | 2020-08-15 | 05:26 | 39.1211 | -122.8612 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | Northshore FD | Circuit ID: 043351103, SAP ID: 102164049 | Y | 12000 | Conductor - Secondary | Overhead | Y | 2020-08-15 | 5:10 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
1715 | PG&E | 2020-08-14 | 16:45 | 37.9842 | -122.0761 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Contra Costa County FD | CGC: 315460554426 | N | 21000 | Transformer | Padmounted | Y | 2020-08-14 | 16:45 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A. |  | EI200814A
1016 | PG&E | 2020-08-14 | 20:20 | 37.1175 | -121.6038 | Building | Urban | 1 meter - < 3 meters | Fire Agency | San Martin FD | Circuit ID: 083242106 | N | 21000 | Conductor - Underground Service | Underground | Y | 2020-08-14 20:18 | 20:18 | Vandalism | N.A. | N.A. | N.A. | Vandalism
1008 | PG&E | 2020-08-14 | 15:02 | 36.9667 | -121.5388 | Other | Urban | 3 meters - 0.25 Acres | Cal Fire | N.A. | CGC: 316964717187; Circuit ID: 083182104 | Y | 21000 | Transformer | Overhead | Y | 2020-08-14 | 14:29 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A. |  | EI200814B
1007 | PG&E | 2020-08-14 | 12:31 | 38.336 | -122.7293 | Other | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Sonoma County FD | Meter: 1010240104 | Y | 750 | Service Drop | Overhead | Y | 2020-08-14 12:56 | 12:30 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
999 | PG&E | 2020-08-13 | 14:14 | 38.1648 | -121.614 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Sacramento FD | Circuit ID: 062462224 | Y | 21000 | Conductor - Open Wire Secondary | Overhead | Y | 2020-08-13 | 14:13 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
997 | PG&E | 2020-08-13 | 10:50 | 38.8158 | -122.0431 | Vegetation | Agriculture | 1 meter - < 3 meters | Customer | N.A. | Circuit ID: 063172101, SAP Pole ID: 101661149 | Y | 21000 | Jumper | Overhead | Y | 2020-08-13 | 10:45 | Contact from object | N.A. | Animal | Jumper | N.A.
996 | PG&E | 2020-08-12 | 21:01 | 38.8513 | -121.3771 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 153701105 | Y | 12000 | Conductor - Primary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
994 | PG&E | 2020-08-12 | 09:52 | 34.9687 | -119.4723 | Other | Herbaceous | 100+ Acres | Fire Agency | Kern County FD | Pole ID: 100190744 | N | 21000 | Jumper | Overhead | Y | 2020-08-12 09:49 | 9:49 | Contact from object | N.A. | Animal | Jumper | N.A.
993 | PG&E | 2020-08-12 | 3:15 | 36.1836 | -119.7173 | Other | Agriculture | 1 meter - < 3 meters | Fire Agency | Kings County FD | Capacitor Bank:161C | Y | 12000 | Capacitor Bank | Overhead | Y | 2020-08-12 02:56 | 2:56 | Contact from object | N.A. | Animal | Capacitor Bank | N.A.
992 | PG&E | 2020-08-11 | 23:48 | 36.7256 | -121.2677 | Vegetation | Barren/Other | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 182492105, Fuse: 4693 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-11 23:39 | 23:39 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
990 | PG&E | 2020-08-11 | 06:34 | 39.5104 | -121.22 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | Cal Fire Butte | Circuit: 103201101, Pole: 100396459 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-11 | 6:15 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
987 | PG&E | 2020-08-10 | 10:20 | 40.4 | -121.939 | Other | Herbaceous | 10 - 100 Acres | Cal Fire | N.A. | 40863458 | N | 500000 | Other | Overhead | N | N.A. | N.A. | Equipment - PG&E | Other | N.A. | N.A. | Other | Induction caused ignition.
986 | PG&E | 2020-08-09 | 08:53 | 39.1191 | -121.0628 | Other | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | 019/150, 019/154 | N | 115000 | Conductor - Transmission | Overhead | Y | 2020-08-09 | 08:53 | Contact from object | N.A. | Animal | Conductor - Transmission | N.A.
981 | PG&E | 2020-08-09 | 17:35 | 37.7234 | -122.0371 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Alco FD | Pole ID: 100901019 Circuit ID: 014091110 | Y | 12000 | Pole | Overhead | Y | 2020-08-09 17:29 | 17:29 | Contact from object | N.A. | Vehicle | Pole | N.A.
976 | PG&E | 2020-08-09 | 00:03 | 40.7983 | -124.1777 | Other | Urban | 1 meter - < 3 meters | Utility - PG&E | PG&E Employee | Pole ID: 100968858 Circuit ID: 192121107 | Y | 12000 | Riser | Overhead | Y | 2020-08-09 00:37 | 0:37 | Equipment - PG&E | Riser Failure | N.A. | N.A. | N.A. |  | EI200809A
975 | PG&E | 2020-08-08 | 20:38 | 39.1082 | -121.6223 | Vegetation | Urban | 1 meter - < 3 meters | Self Extinguished | N.A. | Circuit ID: 153781102 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-08-08 | 20:21 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
969 | PG&E | 2020-08-07 | 15:45 | 36.7067 | -120.4408 | Building | Urban | 3 meters - 0.25 Acres | Cal Fire | N.A. | 252311104 | Y | 750 | Service Drop | Overhead | Y | 2020-08-07 | 15:40 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A. |  | EI200807A
968 | PG&E | 2020-08-07 | 15:45 | 34.7496 | -120.2746 | Vegetation | Urban | 10 - 100 Acres | Fire Agency | Santa Barbara County FD | Pole ID: 101858779 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-08-07 14:54 | 14:54 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
966 | PG&E | 2020-08-07 | 14:03 | 36.8385 | -121.3719 | Other | Herbaceous | 1 meter - < 3 meters | Fire Agency | Hollister FD | Circuit ID: 182492103 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-08-07 13:11 | 13:56 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
963 | PG&E | 2020-08-06 | 13:01 | 36.6636 | -119.7615 | Vegetation | Urban | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 254251108 | Y | 12000 | Conductor - Racked Secondary | Overhead | Y | 2020-08-06 | 12:52 | Contact from object | N.A. | Vegetation | Conductor - Racked Secondary | N.A.
964 | PG&E | 2020-08-05 | 12:39 | 39.4498 | -121.1976 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit: 103201102, Fuse: 1939 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-05 12:41 | 12:41 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
961 | PG&E | 2020-08-05 | 19:40 | 39.8258 | -122.0618 | Vegetation | Agriculture | 0.25 - 10 Acres | Fire Agency | Capay FD | Circuit ID: 102111101 | Y | 750 | Conductor - Secondary | Overhead | Y | 2020-08-05 | 19:34 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
960 | PG&E | 2020-08-05 | 19:05 | 38.3323 | -120.6712 | Other | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire | N.A. | Switch: L5803 | Y | 12000 | Switch | Overhead | Y | 2020-08-05 | 18:49 | Vandalism | N.A. | N.A. | N.A. | Vandalism
958 | PG&E | 2020-08-05 | 11:31 | 40.8939 | -123.5716 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | US Forest Service | Circuit ID: 192171103 Pole ID: 100963292 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-05 11:24 | 11:24 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
957 | PG&E | 2020-08-05 | 7:25 | 38.2654 | -122.7917 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Sonoma County FD | Pole ID: 101987195 Circuit ID: 042631108 | Y | 12000 | Pole | Overhead | Y | 2020-08-05 07:19 | 7:19 | Contact from object | N.A. | Vehicle | Pole | N.A.
955 | PG&E | 2020-08-05 | 02:28 | 40.5632 | -122.3687 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Fire Agency | Redding FD | Circuit ID: 103401102, SAP ID: 101473643 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-05 02:11 | 2:11 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
951 | PG&E | 2020-08-04 | 12:11 | 39.9208 | -122.4535 | Other | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit: 103331102, Pole: 101522530 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-04 11:58 | 11:58 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
1785 | PG&E | 2020-08-03 | 16:38 | 37.3945 | -122.0065 | Other | Urban | 1 meter - < 3 meters | Self Extinguished | N.A. | 83421109 | N | 12000 | Riser | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Balloon | Riser | N.A.
946 | PG&E | 2020-08-03 | 23:15 | 38.8973 | -121.3611 | Other | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Lincoln FD | Circuit ID: 153701105 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-03 23:03 | 23:03 | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
942 | PG&E | 2020-08-03 | 18:43 | 38.6768 | -121.6523 | Other | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | West Sacramento FD | Voltage Regulator: R464 | Y | 12000 | Voltage Regulator | Overhead | Y | 2020-08-03 18:15 | 18:15 | Equipment - PG&E | Voltage Regulator failure | N.A. | N.A. | N.A.
1601 | PG&E | 2020-08-02 | 18:37 | 35.8249 | -120.5452 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 182661104 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-08-02 | 23:38 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
934 | PG&E | 2020-08-02 | 4:19 | 36.8593 | -120.3414 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Transmission pole: 44883391 - 014/174 | N | 115000 | Guy/Span Wire | Overhead | Y | 2020-08-02 | 4:19 | Contact from object | N.A. | Vehicle | Guy/Span Wire | N.A.
931 | PG&E | 2020-08-02 | 16:01 | 34.8381 | -120.2212 | Other | Hardwood Woodland | 0.25 - 10 Acres | Fire Agency | Santa Barbara County FD | Fuse: 6829, 7359, Circuit: 182811102, Pole: 101862714, 101918045 | Y | 12000 | Fuse | Overhead | Y | 2020-08-02 | 15:55 | Equipment - PG&E | Fuse failure - all | N.A. | N.A. | N.A.
930 | PG&E | 2020-08-02 | 23:19 | 37.4142 | -122.1737 | Other | Herbaceous | 0.25 - 10 Acres | Fire Agency | Palo Alto FD | CGC: 315142933707 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-08-02 | 23:18 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
925 | PG&E | 2020-08-02 | 10:13 | 35.3943 | -119.0456 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Bakerfield FD | Transformer CGC: 516886369101 | Y | 12000 | Transformer | Overhead | Y | 2020-08-02 10:10 | 10:10 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
924 | PG&E | 2020-08-02 | 09:52 | 34.6219 | -120.2369 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Santa Barbara County FD | Circuit ID:183041101 | N | 12000 | Automatic Wire Splice | Overhead | Y | 2020-08-02 | 9:37 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
920 | PG&E | 2020-08-01 | 15:42 | 38.8679 | -121.3559 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire | Cal Fire Nevada County FD | Circuit ID: 153701105, SAP ID: 100051057, 100050640 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-08-01 15:35 | 15:35 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
917 | PG&E | 2020-08-01 | 06:14 | 37.6986 | -122.1935 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Alco FD | Circuit ID: 013111106 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-08-01 06:04 | 6:04 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
913 | PG&E | 2020-07-31 | 14:43 | 38.1259 | -122.2414 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Vallejo FD | Circuit ID: 042651106, SAP ID: 102245264 | Y | 12000 | Splice/Clamp/Connector | Overhead | N | N.A. | N.A. | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
910 | PG&E | 2020-07-31 | 03:04 | 39.2065 | -120.9416 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | Cal Fire Nevada County FD | Circuit ID: 152481102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-31 05:17 | 5:18 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
907 | PG&E | 2020-07-30 | 11:20 | 36.0191 | -120.8767 | Other | Herbaceous | 0.25 - 10 Acres | Cal Fire | Cal Fire Bradley Station | Pole ID: 24/374C | N | 60000 | Insulator | Overhead | Y | 2020-07-30 | 11:20 | Equipment - PG&E | Insulator failure | N.A. | N.A. | N.A.
905 | PG&E | 2020-07-29 | 19:24 | 37.3183 | -120.4401 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Merced County FD | Fuse: 8533 | N | 21000 | Fuse | Overhead | Y | 2020-07-29 19:22 | 19:22 | Equipment - PG&E | Fuse failure - all | N.A. | N.A. | N.A.
904 | PG&E | 2020-07-29 | 19:17 | 39.2179 | -121.2396 | Other | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Pole ID: 100010651 | Y | 21000 | Insulator | Overhead | Y | 2020-07-29 19:10 | 19:10 | Contact from object | N.A. | Animal | Insulator | N.A.
903 | PG&E | 2020-07-29 | 17:55 | 38.2445 | -121.4557 | Other | Agriculture | 0.25 - 10 Acres | Fire Agency | Thornton FD | CGC: 317259063657 | N | 12000 | Jumper | Overhead | Y | 2020-07-29 17:45 | 17:45 | Contact from object | N.A. | Animal | Jumper | N.A.
1600 | PG&E | 2020-07-28 | 12:37 | 35.5317 | -120.7292 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 183052111, SAP ID: 101891740 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-28 | 12:31 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
889 | PG&E | 2020-07-28 | 17:14 | 40.6875 | -122.2826 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103561102 | Y | 750 | Conductor - Secondary | Overhead | Y | 2020-07-28 | 17:11 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
887 | PG&E | 2020-07-28 | 13:10 | 39.3937 | -121.2601 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 103201102, Fuse: 1813 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-28 13:03 | 13:03 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
886 | PG&E | 2020-07-28 | 07:18 | 40.4634 | -124.2465 | Other | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished | N.A. | Circuit ID: 192381102 | N | 12000 | Automatic Wire Splice | Overhead | Y | 2020-07-28 16:03 | 16:03 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
890 | PG&E | 2020-07-27 | 06:15 | 38.2107 | -122.2043 | Other | Herbaceous | 10 - 100 Acres | Cal Fire | N.A. | Circuit ID: 042301101 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-07-27 05:51 | 5:51 | Weather | Conductor failure-all | N.A. | N.A. | Weather | High Winds
883 | PG&E | 2020-07-27 | 19:46 | 39.1859 | -122.9776 | Other | Agriculture | 3 meters - 0.25 Acres | Customer | N.A. | Circuit ID: 042871101 | Y | 750 | Conductor - Secondary | Overhead | Y | 2020-07-28 00:15 | 0:15 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
882 | PG&E | 2020-07-27 | 15:32 | 39.0945 | -123.1786 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 042771114, SAP ID: 102198207 | Y | 12000 | Conductor - Primary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
880 | PG&E | 2020-07-26 | 17:51 | 38.195 | -120.6806 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | San Andreas FD | Pole ID: 101250046 | Y | 750 | Crossarm | Overhead | Y | 2020-07-26 18:45 | 17:47 | Equipment - PG&E | Crossarm failure | N.A. | N.A. | N.A.
877 | PG&E | 2020-07-26 | 12:37 | 37.3676 | -120.5902 | Vegetation | Agriculture | 0.25 - 10 Acres | Fire Agency | Merced County FD | SAP Equipment: 40784244; Tower: 013/095 | N | 115000 | Conductor - Transmission | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Balloon | Conductor - Transmission | N.A.
1599 | PG&E | 2020-07-25 | 21:25 | 40.1613 | -122.2975 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103541103 | N | 750 | Conductor - Secondary | Overhead | Y | 2020-07-25 | 21:10 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
875 | PG&E | 2020-07-25 | 09:15 | 35.3382 | -119.0613 | Other | Agriculture | 1 meter - < 3 meters | Fire Agency | Bakersfield FD | Circuit ID: 254072111 Switch: 11005 | N | 21000 | Switch | Underground | Y | 2020-07-25 08:21 | 8:21 | Equipment - PG&E | Switch failure | N.A. | N.A. | N.A. |  | EI200724B
874 | PG&E | 2020-07-24 | 18:05 | 39.1312 | -123.1662 | Other | Urban | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 042771114, SAP ID: 102177888 | Y | 12000 | Transformer | Overhead | N | N.A. | N.A. | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
868 | PG&E | 2020-07-23 | 6:04 | 38.3798 | -120.986 | Other | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 163881101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-23 05:56 | 5:56 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
866 | PG&E | 2020-07-22 | 13:14 | 36.189 | -119.5634 | Other | Herbaceous | 3 meters - 0.25 Acres | Customer | N.A. | Capacitor: 5C | N | 12000 | Capacitor Bank | Overhead | Y | 2020-07-22 13:05 | 13:05 | Contact from object | N.A. | Animal | Capacitor Bank | N.A.
865 | PG&E | 2020-07-22 | 11:42 | 38.9549 | -121.3579 | Other | Urban | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 152811104 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-07-22 11:12 | 11:20 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
864 | PG&E | 2020-07-22 | 11:30 | 37.9447 | -120.8435 | Other | Urban | 10 - 100 Acres | Fire Agency | Modesto FD | Circuit ID: 162981703, SAP ID: 103180643 | N | 17000 | Pole | Overhead | Y | 2020-07-22 11:27 | 11:27 | Contact from object | N.A. | Vehicle | Pole | N.A.
863 | PG&E | 2020-07-20 | 10:57 | 37.9149 | -121.3762 | Other | Agriculture | 3 meters - 0.25 Acres | Unknown | Unknown - Unprotected Area of San Joaquin County | Pole ID: 102064223 | Y | 12000 | Pole | Overhead | Y | 2020-07-20 11:08 | 11:08 | Contact from object | N.A. | Vehicle | Pole | N.A.
853 | PG&E | 2020-07-20 | 03:52 | 37.8992 | -122.2359 | Vegetation | Rural | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 013801101, Pole ID's: 103634689 & 103634684 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-07-20 03:48 | 3:48 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
855 | PG&E | 2020-07-19 | 10:05 | 39.0899 | -121.1363 | Other | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire | Cal Fire/Higgins FD | Drum-Rio Oso #1 115kV Conductor, Tower: 023/176 | N | 115000 | Conductor - Transmission | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Animal | Conductor - Transmission | N.A.
851 | PG&E | 2020-07-19 | 16:00 | 36.5201 | -121.8318 | Vegetation | Urban | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 182291101 | Y | 12000 | Conductor - Primary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
848 | PG&E | 2020-07-19 | 10:28 | 37.0293 | -119.5069 | Other | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire | N.A. | CGC: 418523261789 | N | 12000 | Bushing Mounted Cutout | Overhead | Y | 2020-07-19 10:06 | 10:06 | Contact from object | N.A. | Animal | Bushing Mounted Cutout | N.A.
847 | PG&E | 2020-07-19 | 00:56 | 37.7211 | -122.1341 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | San Leandro FD | Circuit ID: 013111114 Transformer: 315277144877 | Y | 750 | Riser | Underground | Y | 2020-07-19 00:53 | 0:53 | Equipment - PG&E | Riser Failure | N.A. | N.A. | N.A.
871 | PG&E | 2020-07-18 | 19:47 | 39.5534 | -122.185 | Vegetation | Herbaceous | 1 meter - < 3 meters | Self Extinguished | N.A. | Structure 017/375 | N | 60000 | Conductor - Transmission | Overhead | Y | 2020-07-18 | 19:47 | Contact from object | N.A. | Animal | Conductor - Transmission | N.A.
838 | PG&E | 2020-07-17 | 10:21 | 39.7829 | -121.8697 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Pole ID: 100436662 | Y | 12000 | Pole | Overhead | Y | 2020-07-17 10:16 | 10:16 | Contact from object | N.A. | Vehicle | Pole | N.A.
833 | PG&E | 2020-07-16 | 21:30 | 38.2102 | -122.1441 | Other | Urban | 0.25 - 10 Acres | Fire Agency | Cordelia FD | Circuit: 063801102 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-07-16 21:18 | 21:18 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
832 | PG&E | 2020-07-16 | 17:41 | 37.6359 | -121.573 | Other | Rural | 100+ Acres | Cal Fire | N.A. | Circuit ID: 163091101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-16 17:12 | 17:12 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
825 | PG&E | 2020-07-15 | 15:18 | 37.4223 | -119.9613 | Vegetation | Rural | 10 - 100 Acres | Cal Fire | N.A. | Circuit: 254452102, Pole ID: 101065690 | N | 21000 | Conductor - Primary | Overhead | Y | 2020-07-15 15:16 | 15:16 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A. |  | EI200715A
823 | PG&E | 2020-07-15 | 06:59 | 37.7417 | -121.5258 | Vegetation | Urban | 0.25 - 10 Acres | Fire Agency | Tracy FD | Pole ID: 102063891 | N | 12000 | Pole | Overhead | Y | 2020-07-15 06:54 | 6:45 | Contact from object | N.A. | Vehicle | Pole | N.A.
822 | PG&E | 2020-07-14 | 15:59 | 38.3767 | -120.8651 | Other | Rural | 3 meters - 0.25 Acres | Cal Fire | N.A. | Pole ID: 101238524, CGC: 223257026085 | Y | 12000 | Transformer | Overhead | N | N.A. | N.A. | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
820 | PG&E | 2020-07-14 | 11:39 | 37.2991 | -121.9643 | Other | Urban | 1 meter - < 3 meters | Customer | N.A. | Circuit ID: 083371111 | Y | 12000 | Conductor - Secondary | Overhead | Y | 2020-07-14 | 11:37 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
813 | PG&E | 2020-07-12 | 21:35 | 37.2345 | -121.9311 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Santa Clara FD | Pole ID: 103449878 | Y | 750 | Service Connector | Overhead | Y | 2020-07-12 | 21:11 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
812 | PG&E | 2020-07-12 | 18:09 | 38.2543 | -122.1612 | Other | Urban | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 063801102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-12 | 18:08 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
810 | PG&E | 2020-07-12 | 13:33 | 40.1448 | -123.9824 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | PG&E Employee/Cal Fire | Circuit ID: 192221102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-12 14:44 | 14:50 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
809 | PG&E | 2020-07-12 | 04:44 | 40.4178 | -122.2494 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Cottonwood FD | 58/524 | N | 230000 | Insulator | Overhead | Y | 2020-07-12 | 03:16 | Equipment - PG&E | Insulator | N.A. | N.A. | N.A.
806 | PG&E | 2020-07-11 | 19:58 | 37.1937 | -119.4955 | Vegetation | Rural | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 252521103 Pole ID: 103811464 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-11 20:03 | 20:03 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
803 | PG&E | 2020-07-11 | 19:32 | 38.8848 | -120.9961 | Other | Rural | 1 meter - < 3 meters | Fire Agency | Placer County FD | Circuit ID: 152282101 Pole ID: 100049376 | Y | 21000 | Insulator | Overhead | Y | 2020-07-11 19:23 | 19:23 | Contact from object | N.A. | Animal | Insulator | N.A.
800 | PG&E | 2020-07-11 | 09:34 | 35.671 | -120.7371 | Other | Agriculture | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID:182611103 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-07-11 07:59 | 7:59 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
816 | PG&E | 2020-07-10 | 06:08 | 38.1334 | -122.2536 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Vallejo FD | Circuit ID:042651106 ,CGC:219273916999 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-10 05:51 | 5:51 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
799 | PG&E | 2020-07-10 | 20:36 | 38.8087 | -121.4513 | Other | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 152151103, SAP ID: 100085734, 41361151 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-10 20:33 | 20:33 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
796 | PG&E | 2020-07-10 | 00:43 | 39.1721 | -123.7452 | Other | Rural | 1 meter - < 3 meters | Cal Fire | N.A. | Regulator: R599 | N | 12000 | Voltage Regulator | Overhead | N | N.A. | N.A. | Equipment - PG&E | Voltage Regulator failure | N.A. | N.A. | N.A.
795 | PG&E | 2020-07-09 | 19:25 | 38.4025 | -121.9055 | Other | Agriculture | 0.25 - 10 Acres | Fire Agency | Vacaville FD | Circuit ID: 063591103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-09 19:06 | 19:06 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
794 | PG&E | 2020-07-09 | 15:36 | 37.2991 | -122.0139 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Cupertino FD | Circuit ID: 083371113 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-09 15:32 | 15:32 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
792 | PG&E | 2020-07-09 | 13:11 | 40.5411 | -124.064 | Other | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | CircuitID: 192291121 | Y | 12000 | Automatic Wire Splice | Overhead | Y | 2020-07-09 13:06 | 13:06 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
791 | PG&E | 2020-07-09 | 09:38 | 39.7047 | -121.8351 | Other | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103081107, SAP ID: 100345462 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-09 | 9:28 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
790 | PG&E | 2020-07-09 | 4:11 | 38.0902 | -121.1817 | Other | Agriculture | 1 meter - < 3 meters | Fire Agency | Lockeford FD | Circuit ID: 163151101, Fuse: 4579 | Y | 12000 | Fuse | Overhead | Y | 2020-07-09 04:17 | 4:17 | Equipment - PG&E | Fuse failure - all | N.A. | N.A. | N.A.
789 | PG&E | 2020-07-08 | 07:14 | 37.5599 | -120.3234 | Other | Rural | 3 meters - 0.25 Acres | Utility - PG&E | PG&E Employee | Transmission pole: 011/002 Circuit: Merced Falls - Exchequer - 70kv | N | 70000 | Conductor - Primary | Overhead | Y | 2020-07-08 | 7:14 | Contact from object | N.A. | Other | Conductor - Primary | Human Error | Contractor operating excavator caused boom to make contact with tranmission line.
786 | PG&E | 2020-07-07 | 23:16 | 36.531 | -119.4304 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Tulare County FD | Circuit ID:254091104 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-07 23:07 | 23:07 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
775 | PG&E | 2020-07-06 | 23:11 | 38.9111 | -121.1034 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 152461103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-06 22:56 | 23:01 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
773 | PG&E | 2020-07-06 | 23:08 | 35.6474 | -120.5611 | Other | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 183052109, Circuit: Templeton 2109, Pole ID: 103117171, WIP Object ID: 2310819 | Y | 21000 | Pole | Overhead | Y | 2020-07-06 22:57 | 22:57 | Contact from object | N.A. | Vehicle | Pole | N.A.
771 | PG&E | 2020-07-06 | 21:34 | 40.6125 | -122.4942 | Other | Urban | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 103451101 Pole ID:103971310 | Y | 12000 | Service Drop | Overhead | Y | 2020-07-06 | 21:33 | Contact from object | N.A. | Vegetation | Service Drop | N.A. |  | EI200706A
742 | PG&E | 2020-07-05 | 17:20 | 38.8936 | -122.7411 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 043311102 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-07-05 17:14 | 17:14 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
732 | PG&E | 2020-07-05 | 12:15 | 35.5647 | -120.2636 | Other | Agriculture | 10 - 100 Acres | Cal Fire | N.A. | Circuit ID: 182561101, SAP ID: 101907847, CGC: 513268775882 | Y | 21000 | Transformer | Overhead | Y | 2020-07-05 | 12:04 | Contact from object | N.A. | Animal | Transformer | N.A.
1792 | PG&E | 2020-07-05 | 10:45 | 37.5229 | -122.3484 | Vegetation | Urban | Unknown | Unknown | N.A. | 100302414 | Y | 12000 | Transformer | Overhead | N | N.A. | N.A. | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
1598 | PG&E | 2020-07-03 | 02:10 | 39.7622 | -121.8819 | Vegetation | Urban | 3 meters - 0.25 Acres | Unknown | N.A. | Circuit ID: 103071106, SAP ID: 100350713, 100438637 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-03 | 2:01 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
755 | PG&E | 2020-07-03 | 05:33 | 38.463 | -121.1412 | Other | Rural | 10 - 100 Acres | Cal Fire | Cal Fire/Sac Metro/Wilton FD | Towers: 49/303, 49/304, Circuit: Gold Hill-Bellota-Lockeford | N | 115000 | Conductor - Primary | Overhead | Y | 2020-07-03 | 05:33 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
716 | PG&E | 2020-07-03 | 23:32 | 37.7883 | -120.7877 | Other | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 163711701, SAP ID: 103768910 | Y | 17000 | Pole | Overhead | Y | 2020-07-03 | 23:23 | Contact from object | N.A. | Vehicle | Pole | N.A.
715 | PG&E | 2020-07-03 | 19:21 | 34.8208 | -120.2887 | Other | Barren/Other | 0.25 - 10 Acres | Fire Agency | Santa Barbara County FD | Circuit ID: 183031101, SAP ID: 101859251, 101859253 | Y | 12000 | Pole | Overhead | Y | 2020-07-03 19:16 | 19:26 | Contact from object | N.A. | Vehicle | Pole | N.A.
713 | PG&E | 2020-07-03 | 06:18 | 39.7404 | -122.2092 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | Orland FD | Pole ID: 100367889 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-07-03 06:14 | 6:14 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1597 | PG&E | 2020-07-02 | 9:00 | 40.3396 | -123.8706 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished | N.A. | Circuit ID: 192311141 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-07-02 | 10:01 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
706 | PG&E | 2020-07-01 | 06:19 | 35.635 | -118.967 | Other | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished | N.A. | Circuit ID: 253642101 | N | 21000 | Conductor - Primary | Overhead | Y | 2020-07-01 06:39 | 6:04 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
1796 | PG&E | 2020-06-30 | 16:24 | 38.0842 | -121.1513 | Vegetation | Agriculture | 0.25 - 10 Acres | Fire Agency | LINDEN AND PETERS FD | 102102126 | Unknown | 21000 | Transformer | Overhead | Y | 2020-06-30 | 16:17 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
703 | PG&E | 2020-06-30 | 01:38 | 37.962 | -121.3297 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Stockton FD | Circuit ID: 163071102 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-06-30 01:30 | 1:30 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
701 | PG&E | 2020-06-29 | 19:58 | 37.5976 | -122.035 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | Alameda County FD | Pole ID:103775406, CB: TV464 | Y | 12000 | Capacitor Bank | Overhead | Y | 2020-06-29 20:16 | 19:55 | Equipment - PG&E | Capacitor bank failure | N.A. | N.A. | N.A.
700 | PG&E | 2020-06-29 | 18:20 | 38.1548 | -121.7229 | Other | Agriculture | 0.25 - 10 Acres | Fire Agency | Montezuma FD | Circuit ID: 063642107, SAP: 101566838, 101566843 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-29 18:13 | 18:13 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
696 | PG&E | 2020-06-29 | 11:19 | 37.348 | -119.7149 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 254421101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-29 11:30 | 11:30 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
695 | PG&E | 2020-06-29 | 09:56 | 39.8971 | -122.1816 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103331103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-29 09:34 | 9:34 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
694 | PG&E | 2020-06-29 | 6:21 | 38.3107 | -121.869 | Other | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Vacaville FD | Circuit ID: 063642105 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-06-29 06:19 | 6:19 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
693 | PG&E | 2020-06-28 | 17:35 | 36.0072 | -120.122 | Other | Agriculture | 0.25 - 10 Acres | Fire Agency | Avenal FD | Circuit ID: 255002101 | Y | 21000 | Jumper | Overhead | Y | 2020-06-28 | 17:33 | Contact from object | N.A. | Animal | Jumper | N.A.
692 | PG&E | 2020-06-28 | 15:32 | 41.0435 | -124.1076 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 192231101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-28 | 16:37 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
686 | PG&E | 2020-06-28 | 07:58 | 38.7583 | -121.4977 | Other | Agriculture | 0.25 - 10 Acres | Fire Agency | Pleasant Grove FD | Transformer: 221435739785 | Y | 12000 | Transformer | Overhead | Y | 2020-06-28 07:51 | 7:51 | Contact from object | N.A. | Animal | Transformer | N.A.
685 | PG&E | 2020-06-27 | 17:23 | 35.3795 | -118.9573 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Bakersfield FD | Circuit ID: 252771106 | Y | 750 | Conductor - Secondary | Overhead | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
684 | PG&E | 2020-06-27 | 15:41 | 37.6985 | -122.0206 | Other | Urban | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 014091110 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-27 | 15:28 | Contact from object | N.A. | Other | Conductor - Primary | Outside Force | Third party drone flew into primary circuit.
683 | PG&E | 2020-06-27 | 15:01 | 39.7758 | -121.8584 | Other | Urban | 0.25 - 10 Acres | Fire Agency | Chico FD | Capacitor:320 Circuit: Sycamore Creek 1111 | Y | 12000 | Fuse | Overhead | Y | 2020-06-27 15:24 | 15:24 | Equipment - PG&E | Fuse failure - all | N.A. | N.A. | N.A.
682 | PG&E | 2020-06-27 | 14:07 | 36.2747 | -119.7987 | Vegetation | Agriculture | 10 - 100 Acres | Fire Agency | Kings County FD/Lemoore FD | 214C | Y | 12000 | Capacitor Bank | Overhead | Y | 2020-06-27 | 14:01 | Equipment - PG&E | Capacitor bank failure | N.A. | N.A. | N.A.
681 | PG&E | 2020-06-27 | 06:47 | 39.2577 | -121.183 | Other | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Pole ID: 100007177 | Y | 21000 | Insulator | Overhead | Y | 2020-06-27 06:34 | 6:34 | Contact from object | N.A. | Animal | Insulator | N.A.
680 | PG&E | 2020-06-27 | 05:56 | 38.3004 | -122.7435 | Other | Rural | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 042271103 Pole ID: 101991222 | Y | 12000 | Insulator | Overhead | Y | 2020-06-27 | 3:34 | Equipment - PG&E | Insulator failure | N.A. | N.A. | N.A.
679 | PG&E | 2020-06-27 | 03:56 | 38.258 | -122.7817 | Other | Rural | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit: 042631108 Pole ID:102008157 | Y | 12000 | Insulator | Overhead | N | N.A. | N.A. | Equipment - PG&E | Insulator | N.A. | N.A. | N.A.
472 | PG&E | 2020-06-27 | 02:21 | 38.7156 | -122.0471 | Other | Agriculture | 1 meter - < 3 meters | Unknown | N.A. | Pole ID: 101604307 | Y | 21000 | Pole | Overhead | Y | 2020-06-27 | 2:15 | Contact from object | N.A. | Vehicle | Pole | N.A.
676 | PG&E | 2020-06-26 | 17:53 | 36.7855 | -119.7752 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Fresno FD | Circuit ID:253921102 | Y | 12000 | Conductor - Secondary | Overhead | Y | 2020-06-26 | 17:45 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
675 | PG&E | 2020-06-26 | 17:14 | 40.887 | -122.3692 | Other | Urban | 0.25 - 10 Acres | Fire Agency | US Forest Service | Circuit ID: 103271101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-26 17:11 | 17:23 | Contact from object | N.A. | Other | Conductor - Primary | Human Error | Gun shot
672 | PG&E | 2020-06-26 | 05:57 | 40.0209 | -122.4478 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire | N.A. | CGC 118749325087 | N | 12000 | Transformer | Overhead | N | N.A. | N.A. | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
668 | PG&E | 2020-06-25 | 15:05 | 37.9405 | -122.0524 | Other | Urban | 3 meters - 0.25 Acres | Self Extinguished | N.A. | Circuit ID: 014302103 | Y | 21000 | Splice/Clamp/Connector | Overhead | Y | 2020-06-25 | 15:01 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
666 | PG&E | 2020-06-25 | 00:40 | 36.7873 | -119.7713 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Fresno FD | Pole ID: 100867001 | Y | 12000 | Pothead | Overhead | Y | 2020-06-25 00:32 | 0:32 | Equipment - PG&E | Riser Failure | N.A. | N.A. | N.A.
1799 | PG&E | 2020-06-24 | 0:38 | 36.2092 | -120.3015 | Other | Desert Shrub | 1 meter - < 3 meters | Unknown | N.A. | 252381106 | Unknown | 12000 | Conductor - All | Overhead | Y | 2020-06-23 | 23:49 | Contact from object | N.A. | Vehicle | Conductor - All | N.A.
674 | PG&E | 2020-06-24 | 23:48 | 38.0186 | -121.6079 | Other | Agriculture | 3 meters - 0.25 Acres | Utility - PG&E | PG&E Employee | Circuit ID: 014592112 | Y | 21000 | Conductor - Secondary | Overhead | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
661 | PG&E | 2020-06-24 | 11:38 | 39.2652 | -121.546 | Other | Agriculture | 1 meter - < 3 meters | Self Extinguished | N.A. | Circuit ID: 103211102, SAP Eqp ID: 44667592 | N | 12000 | Voltage Regulator | Overhead | Y | 2020-06-24 11:33 | 11:33 | Contact from object | N.A. | Animal | Voltage Regulator | N.A.
658 | PG&E | 2020-06-23 | 20:48 | 39.2133 | -121.2065 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Fire Agency | Penn Valley FD | Circuit ID: 153132105 | Y | 21000 | Conductor - Secondary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
657 | PG&E | 2020-06-23 | 20:47 | 37.2271 | -119.6733 | Other | Rural | 3 meters - 0.25 Acres | Customer | N.A. | Circuit ID: 254432102 | N | 21000 | Splice/Clamp/Connector | Overhead | Y | 2020-06-23 | 20:33 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
656 | PG&E | 2020-06-23 | 20:12 | 39.0524 | -121.0371 | Vegetation | Rural | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 152691110 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-23 19:50 | 19:50 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
655 | PG&E | 2020-06-23 | 16:24 | 40.4881 | -122.5384 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103401101 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-06-23 16:19 | 16:19 | Contact from object | N.A. | Other | Conductor - Primary | Human Error | Clearance issue with street light instalation.
653 | PG&E | 2020-06-23 | 13:00 | 36.6839 | -119.7371 | Vegetation | Urban | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 254251108 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-06-23 | 12:38 | Contact from object | N.A. | Other | Conductor - Primary | Weather | Gusty winds caused material from recycling yard to make contact with primary circuit.
1800 | PG&E | 2020-06-22 | 13:28 | 38.5271 | -122.7963 | Other | Herbaceous | 0.25 - 10 Acres | Fire Agency | Windsor FD | 103838589 | Y | 750 | Conductor - Racked Secondary | Overhead | Y | 2020-06-22 | 13:23 | Contact from object | N.A. | Animal | Conductor - Racked Secondary | N.A.
660 | PG&E | 2020-06-22 | 12:39 | 37.9976 | -121.3025 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Stockton FD | 102138709 | Y | 12000 | Conductor - Secondary | Overhead | Y | 2020-06-22 12:32 | 12:32 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A. |  | EI200622B
651 | PG&E | 2020-06-22 | 22:31 | 40.3492 | -124.0202 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 192251102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-22 21:48 | 22:24 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
648 | PG&E | 2020-06-22 | 21:10 | 35.2153 | -119.3912 | Other | Urban | 1 meter - < 3 meters | Customer | N.A. | CircuitID: 252441104 | Y | 12000 | Service Drop | Overhead | Y | 2020-06-22 | 20:57 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
644 | PG&E | 2020-06-22 | 15:14 | 36.787 | -120.3706 | Other | Agriculture | 0.25 - 10 Acres | Fire Agency | Firebaugh FD | Pole ID: 103900777 | Y | 12000 | Pole | Overhead | Y | 2020-06-22 | 14:47 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A.
641 | PG&E | 2020-06-22 | 13:59 | 37.3684 | -120.4943 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire | N.A. | Pole ID:101013271 | Y | 12000 | Fuse | Overhead | Y | 2020-06-22 13:57 | 13:57 | Contact from object | N.A. | Animal | Fuse | N.A.
640 | PG&E | 2020-06-22 | 07:09 | 38.9263 | -121.4204 | Other | Herbaceous | 0.25 - 10 Acres | Cal Fire | Cal Fire Grass Valley | Pole ID: 100034761, Circuit ID: | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-22 | 7:07 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
1801 | PG&E | 2020-06-22 | 6:22 | 35.3396 | -119.1512 | Other | Agriculture | Unknown | Fire Agency | Kern County FD | 100240427 | Unknown | 21000 | Pole | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Animal | Pole | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
1714 | PG&E | 2020-06-21 | 21:30 | 37.6837 | -122.4806 | Building | Urban | Structure Only | Fire Agency | North County Fire Authority | Meter: 1005040526 | N | 750 | Conductor - Underground Service | Underground | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A. |  | EI200621A
638 | PG&E | 2020-06-21 | 23:49 | 35.6161 | -119.6174 | Other | Rural | 3 meters - 0.25 Acres | Self Extinguished | N.A. | Circuit ID: 254202104 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-06-21 23:04 | 23:04 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
636 | PG&E | 2020-06-21 | 18:04 | 37.3264 | -121.8402 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | San Jose FD | Circuit ID: 082012102 | Y | 21000 | Conductor - Secondary | Overhead | Y | 2020-06-21 | 18:03 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
635 | PG&E | 2020-06-21 | 17:32 | 36.8632 | -121.4911 | Other | Rural | 10 - 100 Acres | Cal Fire | N.A. | Circuit ID: 182742102 | N | 21000 | Conductor - Primary | Overhead | Y | 2020-06-21 | 17:04 | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
632 | PG&E | 2020-06-21 | 08:38 | 36.8058 | -121.3753 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Hollister FD | Circuit ID: 183221111 | Y | 12000 | Fuse | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Animal | Fuse | N.A.
629 | PG&E | 2020-06-20 | 17:24 | 39.365 | -121.5511 | Other | Wetland | 10 - 100 Acres | Cal Fire | N.A. | Pole ID: 100414748 CircuitID: 103211101 | Y | 12000 | Splice/Clamp/Connector | Overhead | N | N.A. | N.A. | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
628 | PG&E | 2020-06-20 | 17:00 | 36.523 | -121.4648 | Other | Rural | 1 meter - < 3 meters | Fire Agency | Gonzalez FD | Circuit ID: 182131104 | Y | 12000 | Jumper | Overhead | Y | 2020-06-20 | 16:58 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
627 | PG&E | 2020-06-20 | 11:42 | 37.7116 | -120.1928 | Other | Rural | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 252192105 | N | 21000 | Splice/Clamp/Connector | Overhead | Y | 2020-06-20 | 11:32 | Equipment - PG&E | Riser Failure | N.A. | N.A. | N.A.
622 | PG&E | 2020-06-19 | 11:49 | 38.7887 | -121.7219 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Woodland FD | GCG 220797240867 | N | 12000 | Splice/Clamp/Connector | Overhead | N | N.A. | N.A. | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
621 | PG&E | 2020-06-19 | 11:58 | 39.489 | -121.5511 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Oroville FD | Recloser: 41270 | Y | 12000 | Recloser | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Animal | Recloser | N.A.
620 | PG&E | 2020-06-19 | 09:16 | 38.9036 | -121.4139 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Unknown | N.A. | Pole ID: 100042731 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-06-19 | 9:14 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
618 | PG&E | 2020-06-19 | 04:37 | 38.4181 | -120.8222 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Agency | Amador FD | Circuit ID: 163541101 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-06-19 04:30 | 4:30 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
614 | PG&E | 2020-06-18 | 18:17 | 38.3687 | -122.4101 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 043292103 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-06-18 16:51 | 16:51 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
611 | PG&E | 2020-06-18 | 16:06 | 38.8904 | -121.3536 | Other | Herbaceous | 10 - 100 Acres | Cal Fire | N.A. | CircuitID: 153701105 Fuse: 8331 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-18 15:51 | 15:51 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
610 | PG&E | 2020-06-18 | 14:26 | 37.4633 | -121.868 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | Milpitas FD | Circuit ID: 082831105 at Pole ID: 100619787 | N | 12000 | Service Drop | Overhead | Y | 2020-06-18 | 14:25 | Contact from object | N.A. | Vehicle | Service Drop | N.A.
608 | PG&E | 2020-06-18 | 06:01 | 38.3405 | -120.7175 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 162161101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-18 05:43 | 6:04 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
603 | PG&E | 2020-06-17 | 12:55 | 39.1309 | -121.5519 | Vegetation | Urban | 3 meters - 0.25 Acres | Customer | N.A. | Circuit ID: 152011108 | Y | 750 | Service Drop | Overhead | Y | 2020-06-17 | 12:51 | Contact from object | N.A. | Vegetation | Service Drop | N.A.
601 | PG&E | 2020-06-17 | 11:19 | 38.9664 | -122.6267 | Other | Urban | 1 meter - < 3 meters | Customer | N.A. | Circuit ID: 043361102 Transformer: 218221047384 | Y | 12000 | Conductor - Secondary | Underground | Y | 2020-06-17 | 11:14 | Equipment - PG&E | Riser Failure | N.A. | N.A. | N.A.
1595 | PG&E | 2020-06-16 | 11:58 | 38.5568 | -122.4544 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 043432104, SAP ID: 103160535 | Y | 750 | Service Drop | Overhead | Y | 2020-06-16 | 11:57 | Contact from object | N.A. | Vegetation | Service Drop | N.A.
594 | PG&E | 2020-06-16 | 15:49 | 39.1254 | -122.995 | Vegetation | Rural | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 042871101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-16 15:38 | 13:36 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
590 | PG&E | 2020-06-15 | 15:38 | 38.8527 | -121.1775 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | Penryn FD | CGC: 222344443296 | N | 12000 | Transformer | Overhead | Y | 2020-06-15 | 15:37 | Contact from object | N.A. | Animal | Transformer | N.A.
589 | PG&E | 2020-06-15 | 10:49 | 35.0092 | -119.0675 | Other | Herbaceous | 10 - 100 Acres | Fire Agency | Kern County FD | Circuit ID: 253411106 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-06-15 05:55 | 8:01 | Contact from object | N.A. | Other | Conductor - Primary | Outside Force | Kite made contact with overhea primary circuit.
1803 | PG&E | 2020-06-15 | 9:57 | 35.0092 | -119.0676 | Other | Herbaceous | Unknown | Utility - PG&E | PG&E Employee | 100221433 | Unknown | 12000 | Conductor - Primary | Overhead | Y | 2020-06-15 | 5:55 | Contact from object | N.A. | Other | Conductor - Primary | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
585 | PG&E | 2020-06-14 | 12:51 | 34.6358 | -120.2818 | Vegetation | Rural | 100+ Acres | Fire Agency | Santa Barbara County FD | Circuit ID: 183041101 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-06-14 12:39 | 12:39 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A. |  | EI200614A
584 | PG&E | 2020-06-13 | 17:46 | 38.7943 | -123.0225 | Vegetation | Urban | 3 meters - 0.25 Acres | Customer | N.A. | Circuit ID: 042821101 | Y | 12000 | Conductor - Racked Secondary | Overhead | Y | 2020-06-13 | 17:36 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
583 | PG&E | 2020-06-13 | 8:28 | 37.6486 | -121.7209 | Other | Rural | 3 meters - 0.25 Acres | Fire Agency | Livermore FD | Circuit ID: 013751102 Pole ID: 100953822 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-13 08:24 | 8:24 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
582 | PG&E | 2020-06-13 | 6:59 | 35.493 | -120.2132 | Other | Rural | 0.25 - 10 Acres | Cal Fire | N.A. | Pole: 101939254 Circuit ID: 182562102 | Y | 21000 | Jumper | Overhead | N | N.A. | N.A. | Equipment - PG&E | Capacitor bank failure | N.A. | N.A. | N.A.
580 | PG&E | 2020-06-12 | 18:04 | 36.5851 | -119.4576 | Vegetation | Urban | 1 meter - < 3 meters | Self Extinguished | N.A. | Circuit ID: 254531107 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-12 17:54 | 17:54 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
579 | PG&E | 2020-06-12 | 14:55 | 40.5026 | -122.4513 | Vegetation | Rural | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 103401101 | Y | 12000 | Conductor - Secondary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
578 | PG&E | 2020-06-12 | 12:29 | 37.1859 | -120.59 | Other | Herbaceous | 0.25 - 10 Acres | Fire Agency | Merced FD | R5418 | Y | 12000 | Voltage Regulator | Overhead | Y | 2020-06-12 13:11 | 13:11 | Equipment - PG&E | Voltage Regulator failure | N.A. | N.A. | N.A.
575 | PG&E | 2020-06-11 | 19:58 | 35.07 | -119.1307 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Kern County FD | Circuit ID: 253411103 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-06-11 19:51 | 19:51 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A. |  | EI200611A
571 | PG&E | 2020-06-11 | 10:49 | 39.9074 | -122.0857 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Pole ID: 101501232 | Y | 12000 | Guy/Span Wire | Overhead | Y | 2020-06-11 10:36 | 10:36 | Contact from object | N.A. | Vehicle | Guy/Span Wire | N.A.
570 | PG&E | 2020-06-11 | 08:11 | 36.4392 | -119.4258 | Vegetation | Rural | 3 meters - 0.25 Acres | Self Extinguished | N.A. | Circuit ID: 254091105 | N | 12000 | Pole | Overhead | Y | 2020-06-11 07:55 | 7:55 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A.
1594 | PG&E | 2020-06-10 | 16:15 | 38.5844 | -122.6612 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 042711101, SAP ID: 102220153 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-10 | 16:10 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1593 | PG&E | 2020-06-10 | 13:09 | 38.5462 | -122.3501 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 043432104, SAP ID: 102262620, 102262624, 102262626 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-10 | 12:30 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
569 | PG&E | 2020-06-10 | 23:59 | 37.7646 | -121.5845 | Other | Rural | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 163741102, Pole ID: 102051395 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-10 23:46 | 23:46 | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
567 | PG&E | 2020-06-10 | 16:51 | 38.5896 | -121.7141 | Vegetation | Agriculture | 1 meter - < 3 meters | Fire Agency | Davis FD | R698 | Y | 12000 | Voltage Regulator | Overhead | Y | 2020-06-10 17:12 | 17:12 | Equipment - PG&E | Voltage Regulator failure | N.A. | N.A. | N.A.
563 | PG&E | 2020-06-10 | 05:31 | 37.4251 | -119.958 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire | N.A. | 254452102 | N | 21000 | Conductor - Primary | Overhead | Y | 2020-06-10 05:29 | 5:29 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
555 | PG&E | 2020-06-09 | 14:18 | 37.9994 | -121.225 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Morada FD | Pole ID: 102134997 | Y | 750 | Splice/Clamp/Connector | Overhead | N | N.A. | N.A. | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
542 | PG&E | 2020-06-08 | 09:37 | 38.3075 | -122.4961 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Sonoma FD | Circuit ID: 042721104 | Y | 12000 | Conductor - Secondary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vehicle | Conductor - Secondary | N.A.
541 | PG&E | 2020-06-08 | 09:23 | 37.3161 | -120.4558 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Merced FD | Circuit ID: 252802101 | Y | 750 | Conductor - Open Wire Secondary | Overhead | Y | 2020-06-08 09:45 | 9:45 | Weather | Conductor failure-all | N.A. | N.A. | Weather | High Winds
540 | PG&E | 2020-06-07 | 22:32 | 38.3767 | -122.8137 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Agency | Goldridge Fire Department | Circuit ID:042571104 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-07 | 21:58 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
537 | PG&E | 2020-06-07 | 16:38 | 38.8324 | -123.6233 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Fire Agency | South Coast FD | Circuit ID: 042841112 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-06-07 16:29 | 16:29 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
533 | PG&E | 2020-06-07 | 11:58 | 36.2799 | -121.0886 | Vegetation | Herbaceous | 100+ Acres | Cal Fire | N.A. | Pole ID: 101729281 | N | 12000 | Tie Wire | Overhead | Y | 2020-06-07 11:48 | 11:48 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
528 | PG&E | 2020-06-06 | 19:41 | 38.1773 | -121.3993 | Vegetation | Rural | 3 meters - 0.25 Acres | Fire Agency | Thornton FD | Circuit ID: 163021103 | Y | 12000 | Conductor - Racked Secondary | Overhead | N | N.A. | N.A. | Weather | Conductor failure-all | N.A. | N.A. | Weather | High Winds
527 | PG&E | 2020-06-06 | 19:07 | 38.266 | -121.6015 | Vegetation | Rural | 3 meters - 0.25 Acres | Fire Agency | Courtland FD | Circuit ID: 062462227 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-06-06 18:16 | 18:16 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
526 | PG&E | 2020-06-06 | 18:18 | 38.6720617 | -121.8998033 | Vegetation | Agriculture | 1 meter - < 3 meters | Fire Agency | Yolo County Fire Department | Circuit ID: 063171103 | Y | 12000 | Jumper | Overhead | Y | 2020-06-06 17:35 | 17:35 | Contact from object | N.A. | Vegetation | Jumper | N.A.
525 | PG&E | 2020-06-06 | 15:30 | 34.6369 | -120.0249 | Vegetation | Herbaceous | 10 - 100 Acres | Fire Agency | Santa Barbara County FD | 182721104 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-06 15:12 | 15:12 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
524 | PG&E | 2020-06-06 | 15:12 | 38.4386 | -122.7323 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | Santa Rosa FD | Circuit ID: 042151106 | Y | 12000 | Conductor - Secondary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
1592 | PG&E | 2020-06-04 | 14:45 | 38.7167 | -121.752 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Woodland FD | Circuit ID: 062031108 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-06-04 | 14:41 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
519 | PG&E | 2020-06-04 | 18:19 | 38.1702 | -120.6673 | Other | Urban | 3 meters - 0.25 Acres | Cal Fire | N.A. | Reg A: 41023521 | N | 60000 | Voltage Regulator | Padmounted | Y | 2020-06-04 18:01 | 18:01 | Equipment - PG&E | Voltage Regulator failure | N.A. | N.A. | N.A. |  | EI200604A
517 | PG&E | 2020-06-04 | 19:50 | 37.2854 | -121.9255 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Santa Clara FD | Circuit ID: 082921104 | Y | 750 | Conductor - Secondary | Overhead | Y | 2020-06-04 | 19:46 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
516 | PG&E | 2020-06-04 | 18:18 | 37.7921 | -121.2018 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Manteca FD | Pole ID: 103177192 | Y | 17000 | Crossarm | Overhead | Y | 2020-06-04 18:43 | 19:05 | Equipment - PG&E | Crossarm failure | N.A. | N.A. | N.A.
514 | PG&E | 2020-06-04 | 09:26 | 37.7154 | -122.1508 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Alameda County FD | CGC: 315227944676 | Y | 12000 | Transformer | Overhead | Y | 2020-06-04 | 9:19 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
513 | PG&E | 2020-06-04 | 05:05 | 37.2737 | -121.7224 | Other | Herbaceous | 10 - 100 Acres | Cal Fire | Cal Fire/Santa Clara County FD/San Jose FD | Circuit: TESLA-METCALF-500kV Conductor, Tower: 40587595 | N | 500000 | Conductor - Transmission | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Balloon | Conductor - Transmission | N.A. |  | EI200604B
508 | PG&E | 2020-06-03 | 14:55 | 37.349 | -122.1053 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Los Altos FD | Circuit ID: 082161102 | Y | 12000 | Splice/Clamp/Connector | Overhead | N | N.A. | N.A. | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
507 | PG&E | 2020-06-03 | 14:35 | 38.1322 | -121.1425 | Other | Rural | 0.25 - 10 Acres | Fire Agency | Stockton FD | Circuit ID: 163682102 Pole ID:102079114, 102079112,102079107, 102079078, 102079096 Transformers: 318155059490, 318151059407, 318155259620 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-06-03 14:22 | 14:21 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
505 | PG&E | 2020-06-03 | 10:35 | 35.5724 | -119.357 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Kern County FD | Pole ID: 100123689 | N | 12000 | Guy/Span Wire | Overhead | Y | 2020-06-03 10:19 | 10:19 | Contact from object | N.A. | Vehicle | Guy/Span Wire | N.A.
503 | PG&E | 2020-06-03 | 06:58 | 35.1946 | -118.7645 | Other | Herbaceous | 0.25 - 10 Acres | Fire Agency | Arvin FD | L420 | N | 12000 | Capacitor Bank | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Animal | Capacitor Bank | N.A.
502 | PG&E | 2020-06-02 | 21:07 | 36.6402 | -119.3882 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 252341106, SAP ID: 100738071 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-06-02 | 20:55 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
498 | PG&E | 2020-06-02 | 15:50 | 36.3136 | -119.764 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Kings County FD | 217C | N | 12000 | Capacitor Bank | Overhead | Y | 2020-06-02 | 15:48 | Equipment - PG&E | Capacitor bank failure | N.A. | N.A. | N.A.
497 | PG&E | 2020-06-02 | 13:58 | 38.3242 | -122.0207 | Other | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Vaca-Vacaville-Jameson-North Tower near tower 010/076 | N | 12000 | Pole | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Other | Pole | Human Error | Airstrike | EI200602A
496 | PG&E | 2020-06-02 | 11:49 | 37.5991 | -122.0417 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Alameda FD | CAP Bank: TV539 | Y | 12000 | Capacitor Bank | Overhead | Y | 2020-06-02 12:14 | 12:14 | Equipment - PG&E | Capacitor bank failure | N.A. | N.A. | N.A.
495 | PG&E | 2020-06-02 | 10:48 | 35.3878 | -120.8227 | Vegetation | Agriculture | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID 183011101 | N | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-06-02 10:29 | 10:29 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1591 | PG&E | 2020-06-01 | 17:53 | 39.3048 | -121.8504 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Agency | Sutter County FD | Circuit ID: 153771104 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-06-01 | 17:48 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
491 | PG&E | 2020-06-01 | 12:08 | 38.0748 | -122.2295 | Vegetation | Urban | 0.25 - 10 Acres | Fire Agency | Vallejo FD | 719 | N | 12000 | Switch | Overhead | Y | 2020-06-01 | 12:29 | Equipment - PG&E | Switch failure | N.A. | N.A. | N.A.
478 | PG&E | 2020-05-29 | 16:52 | 37.3452 | -121.9139 | Vegetation | Urban | 10 - 100 Acres | Fire Agency | San Jose FD | Circuit ID: 082261116 and 082261117 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-29 16:40 | 16:40 | Weather | Conductor failure-all | N.A. | N.A. | Weather | High Winds
476 | PG&E | 2020-05-29 | 17:52 | 35.5304 | -118.9794 | Other | Rural | 100+ Acres | Fire Agency | Kern County FD | Circuit: Vedder Tap 115kv Pole: 6/72, 4/61, 3/48 | N | 21000 | Insulator | Overhead | Y | 2020-05-29 17:14 | 17:14 | Contact from object | N.A. | Animal | Insulator | N.A.
473 | PG&E | 2020-05-29 | 11:41 | 35.6095 | -120.6255 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | Pole ID: 101940022, GCG: 512198677918, Circuit ID: 183052109 | N | 21000 | Pole | Overhead | Y | 2020-05-29 11:28 | 11:28 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A.
547 | PG&E | 2020-05-28 | 12:47 | 37.5498 | -121.9811 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | Fremont FD | 014351108 | Y | 12000 | Conductor - Secondary | Underground | N | N.A. | N.A. | Contact from object | N.A. | Other | Conductor - Secondary | Human Error | Third party developer made contact and damaged underground conduit.
492 | PG&E | 2020-05-28 | 19:03 | 38.4986 | -122.4316 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 043432102 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-05-28 19:17 | 19:00 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
468 | PG&E | 2020-05-27 | 16:00 | 38.4033 | -122.0406 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Agency | Vacaville Fire Protection District | Pole ID: 103853743; Pole ID: 101666073 | N | 12000 | Pole | Overhead | Y | 2020-05-27 15:56 | 15:56 | Contact from object | N.A. | Vegetation | Pole | N.A.
467 | PG&E | 2020-05-27 | 15:46 | 38.4713 | -120.98 | Vegetation | Shrub | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 163541101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-27 16:08 | 16:08 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
462 | PG&E | 2020-05-27 | 00:58 | 39.0137 | -121.0532 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Fire Agency | Higgins FD | Circuit ID: 152691107 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-27 00:15 | 0:15 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
457 | PG&E | 2020-05-26 | 17:45 | 37.5289 | -121.9883 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Fremont FD | Circuit ID: 12221106, SB 9129 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-26 17:42 | 17:42 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
456 | PG&E | 2020-05-26 | 17:22 | 37.6424 | -122.0834 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Alameda County FD | Pole ID: 100958943 | Y | 12000 | Crossarm | Overhead | Y | 2020-05-26 | 17:21 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
455 | PG&E | 2020-05-26 | 15:59 | 37.5097 | -121.9546 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Fremont FD | Circuit ID: 012222107 | N | 21000 | Splice/Clamp/Connector | Underground | Y | 2020-05-26 15:55 | 15:55 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
454 | PG&E | 2020-05-26 | 14:24 | 36.5142 | -119.2778 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Self Extinguished | N.A. | GCG: 419185242990 | N | 12000 | Transformer | Overhead | Y | 2020-05-26 14:23 | 14:23 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
453 | PG&E | 2020-05-26 | 13:09 | 36.6694 | -119.7368 | Vegetation | Urban | 1 meter - < 3 meters | Customer | N.A. | CGC: 417841248735, CGC: 417841248736, | N | 12000 | Transformer | Overhead | Y | 2020-05-26 12:04 | 12:04 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A.
452 | PG&E | 2020-05-26 | 12:33 | 36.5034 | -120.3919 | Other | Rural | 3 meters - 0.25 Acres | Fire Agency | Cantua Creek FD | Circuit ID: 253591103 | Y | 12000 | Service Drop | Overhead | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
450 | PG&E | 2020-05-26 | 11:23 | 38.2345 | -121.2543 | Vegetation | Rural | 3 meters - 0.25 Acres | Fire Agency | Stockton FD | Circuit ID: 162231102 | Y | 12000 | Splice/Clamp/Connector | Overhead | N | N.A. | N.A. | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
449 | PG&E | 2020-05-25 | 20:52 | 37.4314 | -121.9638 | Vegetation | Herbaceous | 1 meter - < 3 meters | Fire Agency | San Jose FD | Pole ID:100559342 | Y | 21000 | Jumper | Overhead | Y | 2020-05-25 20:42 | 20:42 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
448 | PG&E | 2020-05-25 | 15:16 | 38.4429 | -121.8594 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Unknown | N.A. | 62061106 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-25 15:11 | 15:11 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
442 | PG&E | 2020-05-24 | 13:24 | 36.0688 | -120.2223 | Other | Agriculture | 10 - 100 Acres | Cal Fire | N.A. | CGC: 416390327020 | N | 21000 | Transformer | Overhead | Y | 2020-05-24 13:51 | 13:51 | Contact from object | N.A. | Animal | Transformer | N.A.
440 | PG&E | 2020-05-24 | 07:39 | 37.9814 | -122.0489 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Contra Costa County FD | Circuit ID: 014302110 | Y | 21000 | Conductor - Primary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
437 | PG&E | 2020-05-23 | 11:47 | 35.8618 | -119.9122 | Other | Rural | 10 - 100 Acres | Cal Fire | N.A. | Capacitor: 96C Circuit ID: 252952108 | Y | 12000 | Capacitor Bank | Overhead | Y | 2020-05-23 12:50 | 12:50 | Contact from object | N.A. | Animal | Capacitor Bank | N.A.
433 | PG&E | 2020-05-22 | 18:21 | 39.6629 | -121.7759 | Vegetation | Agriculture | 1 meter - < 3 meters | Fire Agency | Butte County FD | CGC 220634572748 | Y | 12000 | Bushing Mounted Cutout | Overhead | Y | 2020-05-22 18:12 | 18:12 | Contact from object | N.A. | Animal | Bushing Mounted Cutout | N.A.
1812 | PG&E | 2020-05-21 | 13:59 | 36.6594 | -121.6127 | Vegetation | Urban | 0.25 - 10 Acres | Fire Agency | Salinas FD | 182261104 | N | 12000 | Fuse | Overhead | N | N.A. | N.A. | Equipment - PG&E | Fuse failure - all | N.A. | N.A. | N.A.
1658 | PG&E | 2020-05-20 | 15:35 | 38.8961 | -121.2193 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown | N.A. | Circuit ID: 153701101, SAP ID: 100043460 | Y | 12000 | Fuse | Overhead | Y | 2020-05-20 | 15:33 | Contact from object | N.A. | Vegetation | Fuse | N.A.
425 | PG&E | 2020-05-20 | 18:37 | 35.1559 | -119.4842 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Taft FD | Circuit ID: 252081103 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-05-20 18:32 | 18:32 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
415 | PG&E | 2020-05-17 | 15:14 | 36.1317 | -121.0239 | Vegetation | Urban | 10 - 100 Acres | Cal Fire | N.A. | 182191102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-17 15:03 | 15:03 | Weather | Conductor failure-all | N.A. | N.A. | Weather | High Winds
414 | PG&E | 2020-05-17 | 14:11 | 35.3026 | -118.843 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Kern County FD | Pole ID: 100157814 | N | 12000 | Pole | Overhead | Y | 2020-05-17 14:05 | 14:05 | Contact from object | N.A. | Vehicle | Pole | N.A.
411 | PG&E | 2020-05-16 | 05:58 | 38.3146 | -121.8413 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Dixon FD | 63642107 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-05-16 05:55 | 5:55 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
407 | PG&E | 2020-05-14 | 06:51 | 36.1374 | -120.2052 | Other | Herbaceous | 10 - 100 Acres | Cal Fire | N.A. | 9500 | N | 12000 | Recloser | Overhead | Y | 2020-05-14 06:40 | 6:40 | Contact from object | N.A. | Animal | Recloser | N.A.
406 | PG&E | 2020-05-14 | 04:31 | 38.1102 | -122.2186 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Vallejo FD | 042451101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-14 03:59 | 3:59 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
405 | PG&E | 2020-05-14 | 03:29 | 38.2248 | -120.8346 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | 163231101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-14 03:13 | 3:13 | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
1590 | PG&E | 2020-05-12 | 07:49 | 37.2798 | -122.2061 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 024131103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-12 | 5:37 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
400 | PG&E | 2020-05-12 | 12:57 | 36.2693 | -119.691 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | King County FD | 252661104 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-12 12:49 | 12:49 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
398 | PG&E | 2020-05-11 | 8:22 | 37.5059 | -122.2101 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Redwood City FD | Circuit ID: 024261103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-11 08:20 | 8:11 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
397 | PG&E | 2020-05-11 | 16:42 | 35.5832 | -120.4274 | Vegetation | Rural | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 182561101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-11 16:42 | 16:42 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
393 | PG&E | 2020-05-10 | 16:59 | 38.897 | -121.0673 | Other | Urban | 1 meter - < 3 meters | Fire Agency | Auburn FD | Circuit ID: 152161101 | Y | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-05-10 | 16:59 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
387 | PG&E | 2020-05-09 | 18:49 | 39.007 | -122.7816 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Agency | Kelseyville FD | Pole ID: 102160256 | Y | 12000 | Pole | Overhead | Y | 2020-05-09 18:46 | 18:46 | Contact from object | N.A. | Vehicle | Pole | N.A.
385 | PG&E | 2020-05-08 | 15:55 | 37.8684 | -120.4312 | Other | Rural | 0.25 - 10 Acres | Cal Fire | N.A. | Pole ID: 101029227 Circuit ID: 163781701 | Y | 17000 | Pole | Overhead | Y | 2020-05-08 15:46 | 15:46 | Contact from object | N.A. | Vehicle | Pole | N.A.
384 | PG&E | 2020-05-08 | 14:29 | 38.6454 | -121.0295 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | El Dorado Hills FD | Pole ID: 10141282 | Y | 21000 | Pole | Overhead | Y | 2020-05-08 14:24 | 14:24 | Contact from object | N.A. | Vehicle | Pole | N.A.
383 | PG&E | 2020-05-08 | 12:54 | 35.9424 | -120.0914 | Other | Rural | 3 meters - 0.25 Acres | Self Extinguished | N.A. | Capacitor: 156K Circuit ID: 255002101 | Y | 21000 | Capacitor Bank | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Animal | Capacitor Bank | N.A.
378 | PG&E | 2020-05-07 | 17:52 | 37.3241 | -120.6875 | Other | Agriculture | 3 meters - 0.25 Acres | Cal Fire | Merced County Cal Fire | Circuit ID: 253611102 Pole ID: 103981165 | N | 12000 | Pole | Overhead | Y | 2020-05-07 17:48 | 17:48 | Contact from object | N.A. | Vehicle | Pole | N.A.
376 | PG&E | 2020-05-07 | 13:25 | 38.1072 | -121.9888 | Other | Rural | 3 meters - 0.25 Acres | Fire Agency | Suisun FD | Circuit ID: 062701104 | N | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-05-07 14:11 | 14:11 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
1816 | PG&E | 2020-05-06 | 12:39 | 35.4152 | -120.5799 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown | N.A. | 101889816 | N | 750 | Service Connector | Overhead | N | N.A. | N.A. | Equipment - PG&E | Service Neutral failure | N.A. | N.A. | N.A.
370 | PG&E | 2020-05-06 | 22:51 | 38.5289 | -120.8485 | Other | Rural | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 163541102 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-05-06 | 22:24 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
369 | PG&E | 2020-05-06 | 14:11 | 37.0383 | -120.1517 | Other | Urban | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 252421113 | Y | 12000 | Conductor - Secondary | Overhead | Y | 2020-05-06 14:10 | 14:10 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
361 | PG&E | 2020-05-05 | 15:39 | 38.5905 | -122.9383 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire | N.A. | 042751113 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-05 15:37 | 15:37 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
359 | PG&E | 2020-05-05 | 09:55 | 34.5857 | -120.1067 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Santa Barbara County FD | Circuit ID: 182721102 | N | 12000 | Splice/Clamp/Connector | Overhead | Y | 2020-05-05 05:35 | 5:35 | Equipment - PG&E | Splice/Clamp/Connector | N.A. | N.A. | N.A.
357 | PG&E | 2020-05-04 | 18:25 | 38.4857 | -122.7606 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Santa Rosa FD | Circuit ID: 042561107 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-05-04 18:19 | 18:19 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
349 | PG&E | 2020-05-02 | 14:04 | 36.6401 | -119.3862 | Other | Agriculture | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 252341106 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-05-02 14:03 | 14:03 | Contact from object | N.A. | Other | Conductor - Primary | Outside Force | Third party canopy made contact with primary circuit.
348 | PG&E | 2020-05-02 | 11:42 | 34.8869 | -120.4111 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Santa Maria FD | Circuit ID: 182061108 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-02 | 11:41 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
341 | PG&E | 2020-05-01 | 00:56 | 39.6474 | -121.635 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | Guy attached to 103124762 | Y | 12000 | Guy/Span Wire | Overhead | Y | 2020-05-01 00:42 | 0:42 | Contact from object | N.A. | Vehicle | Guy/Span Wire | N.A.
342 | PG&E | 2020-04-30 | 23:35 | 38.0999 | -122.8826 | Vegetation | Rural | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 042291101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-05-01 01:40 | 1:40 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1589 | PG&E | 2020-04-29 | 13:26 | 38.5402 | -122.5857 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 042711101 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-04-29 | 16:24 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
335 | PG&E | 2020-04-29 | 15:25 | 39.5558 | -121.51 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 103091102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-04-29 15:33 | 15:33 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
333 | PG&E | 2020-04-28 | 12:45 | 38.1072 | -121.9888 | Other | Wetland | 3 meters - 0.25 Acres | Utility - PG&E | N.A. | Pole ID: 101559042 Circuit ID: 062701104 | N | 12000 | Conductor - Primary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
331 | PG&E | 2020-04-27 | 14:27 | 36.719 | -120.1327 | Vegetation | Agriculture | 0.25 - 10 Acres | Fire Agency | North Central FD | Pole ID: 100646155 | N | 12000 | Lightning Arrestor | Overhead | Y | 2020-04-27 14:10 | 14:10 | Equipment - PG&E | Lightning arrestor failure | N.A. | N.A. | N.A.
323 | PG&E | 2020-04-25 | 16:10 | 38.2941 | -122.0974 | Other | Agriculture | 1 meter - < 3 meters | Fire Agency | Suisun FD | Circuit ID: 063801105 | Y | 12000 | Service Drop | Overhead | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
321 | PG&E | 2020-04-25 | 04:20 | 38.123 | -121.685 | Other | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Rio Vista FD | Fuse: 12587 | N | 21000 | Fuse | Overhead | Y | 2020-04-25 03:46 | 3:46 | Contact from object | N.A. | Vegetation | Fuse | N.A.
338 | PG&E | 2020-04-23 | 18:05 | 35.1232 | -120.6291 | Building | Urban | Structure Only | Cal Fire | San Luis Obispo | 182601106 | N.A. | 12000 | N.A. | Overhead | N | N.A. | N.A. | Under Investigation | N.A. | N.A. | N.A. | N.A. | PG&E has included the following ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition. | EI200423A
316 | PG&E | 2020-04-23 | 15:33 | 37.8931 | -121.0343 | Vegetation | Herbaceous | 0.25 - 10 Acres | Fire Agency | Farmington FD | Circuit ID: 163571702 | N | 17000 | Conductor - Primary | Overhead | Y | 2020-04-23 15:25 | 15:25 | Contact from object | N.A. | Balloon | Conductor - Primary | N.A.
315 | PG&E | 2020-04-23 | 11:08 | 39.2833 | -121.683 | Other | Rural | 3 meters - 0.25 Acres | Unknown | N.A. | Pole ID: 103792347 Circuit ID: 153771104 | Y | 12000 | Pole | Overhead | Y | 2020-04-23 12:14 | 11:05 | Equipment - PG&E | Pole failure | N.A. | N.A. | N.A.
314 | PG&E | 2020-04-22 | 14:40 | 37.0324 | -120.1205 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire | N.A. | 254611104 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-04-22 14:30 | 14:30 | Unknown | Conductor failure-all | N.A. | N.A. | Unknown | Unknown as to what caused the initial failure, but initial investigation found the ignition to be attributable to PG&E facilities.
308 | PG&E | 2020-04-17 | 20:25 | 37.6834 | -121.2529 | Other | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Lathrop Manteca FD | Circuit ID: 163801704 | Y | 17000 | Conductor - Primary | Overhead | Y | 2020-04-17 20:00 | 20:00 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
299 | PG&E | 2020-04-15 | 16:05 | 39.0968 | -121.7361 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Agency | Sutter County FD | 152111103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-04-15 16:03 | 16:03 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
297 | PG&E | 2020-04-14 | 17:56 | 38.1596 | -121.8073 | Vegetation | Agriculture | 1 meter - < 3 meters | Fire Agency | Suisun FD | Circuit 063642107 | N | 21000 | Service Drop | Overhead | Y | 2020-04-14 | 17:55 | Contact from object | N.A. | Vehicle | Service Drop | N.A.
277 | PG&E | 2020-04-07 | 15:42 | 36.3004 | -121.0489 | Other | Herbaceous | 1 meter - < 3 meters | Cal Fire | N.A. | 182031102 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-04-07 15:38 | 15:38 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
262 | PG&E | 2020-04-03 | 12:19 | 35.5061 | -119.6222 | Other | Agriculture | 0.25 - 10 Acres | Utility - PG&E | PG&E SIPT | 515175973372 | Y | 12000 | Transformer | Overhead | Y | 2020-04-03 12:17 | 12:17 | Contact from object | N.A. | Animal | Transformer | N.A.
260 | PG&E | 2020-04-02 | 15:27 | 38.8032 | -123.5331 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | South Coast FPD | Transmission: ELK-GUALALA-60kV Conductor, Distribution Circuit ID: 042841111 | Y | 60000 | Conductor - Transmission | Overhead | Y | 2020-04-02 15:23 | 15:23 | Contact from object | N.A. | Vegetation | Conductor - Transmission | N.A.
227 | PG&E | 2020-03-17 | 21:47 | 40.6897 | -121.9244 | Building | Shrub | 3 meters - 0.25 Acres | Cal Fire | N.A. | Circuit ID: 103601101 | N | 12000 | Service Drop | Overhead | Y | 2020-03-18 05:59 | 22:42 | Contact from object | N.A. | Vegetation | Service Drop | N.A. |  | EI200317A
212 | PG&E | 2020-03-13 | 16:00 | 38.3598 | -121.9734 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Vacaville FD | Circuit ID: 063601110 | N | 750 | Conductor - Secondary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
1822 | PG&E | 2020-03-12 | 13:08 | 40.0679 | -122.1909 | Other | Agriculture | Unknown | Unknown | N.A. | 103391102 | N | 12000 | Conductor - Primary | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
1827 | PG&E | 2020-03-08 | 15:33 | 35.8764 | -119.6449 | Vegetation | Barren/Other | Unknown | Unknown | N.A. | 252151103 | N | 12000 | Conductor - All | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Conductor - All | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
191 | PG&E | 2020-03-07 | 7:58 | 35.8441 | -120.0492 | Vegetation | Agriculture | 0.25 - 10 Acres | Fire Agency | Kings County FD | Circuit ID: 253451101 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-03-07 11:00 | 11:00 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
189 | PG&E | 2020-03-06 | 14:21 | 37.1742 | -119.7896 | Other | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire | N.A. | Transformer # 931088881 | N | 21000 | Jumper | Overhead | Y | 2020-03-06 14:15 | 14:15 | Contact from object | N.A. | Animal | Jumper | N.A.
188 | PG&E | 2020-03-06 | 1:55 | 36.9681 | -120.0718 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Agency | Madera County FD | 252761104 | N | 12000 | Conductor - Secondary | Overhead | Y | 2020-03-06 05:21 | 5:21 | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
184 | PG&E | 2020-03-05 | 11:43 | 40.2886 | -123.803 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Utility - PG&E | N.A. | Pole ID: 100989601 | N | 12000 | Insulator | Overhead | Y | 2020-03-05 11:40 | 11:40 | Contact from object | N.A. | Vehicle | Insulator | N.A.
174 | PG&E | 2020-03-02 | 1:08 | 38.3485 | -121.9665 | Other | Urban | 3 meters - 0.25 Acres | Fire Agency | Vacaville FD | Circuit ID: 063601107 | Y | 12000 | Conductor - Racked Secondary | Overhead | Y | 2020-03-02 | 0:52 | Weather | Conductor failure-all | N.A. | N.A. | Weather | High Winds
173 | PG&E | 2020-03-02 | 10:56 | 36.7287 | -120.3149 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire | N.A. | Circuit ID: 252311102 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-03-02 10:25 | 10:25 | Contact from object | N.A. | Other | Conductor - Primary | Human Error | Gun Shot
172 | PG&E | 2020-03-02 | 15:51 | 37.2789 | -121.9603 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | Campbell FD | Circuit ID: 083371109 | N | 12000 | Conductor - Secondary | Overhead | Y | 2020-03-02 | 15:35 | Contact from object | N.A. | Vegetation | Conductor - Secondary | N.A.
166 | PG&E | 2020-02-29 | 12:57 | 36.7382 | -121.6081 | Other | Herbaceous | 0.25 - 10 Acres | Fire Agency | Salinas FD | Circuit ID: 182331101; SAP ID: 101711418 | Y | 60000 | Conductor - Primary | Overhead | Y | 2020-02-29 12:51 | 12:58 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A. |  | EI200229A
138 | PG&E | 2020-02-21 | 6:58 | 35.2816 | -118.941 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Self Extinguished | N.A. | 14951 | N | 12000 | Fuse | Overhead | Y | 2020-02-21 07:36 | 7:36 | Equipment - PG&E | Fuse failure - all | N.A. | N.A. | N.A.
121 | PG&E | 2020-02-14 | 9:45 | 36.631 | -119.6094 | Other | Agriculture | 1 meter - < 3 meters | Cal Fire | N.A. | Circuit ID: 254121101 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-02-14 10:13 | 10:13 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.
115 | PG&E | 2020-02-13 | 10:09 | 37.7414 | -121.4228 | Building | Urban | 3 meters - 0.25 Acres | Fire Agency | City of Tracy FD | Meter: 1006243555 | Y | 12000 | Service Drop | Overhead | Y | 2020-02-13 10:35 | 10:35 | Contact from object | N.A. | Vegetation | Service Drop | N.A. |  | EI200213A
110 | PG&E | 2020-02-11 | 19:42 | 36.7655 | -119.7529 | Vegetation | Urban | 1 meter - < 3 meters | Fire Agency | Fresno FD | Circuit ID 253571106; pole id 103293183 | Y | 750 | Service Drop | Overhead | N | N.A. | N.A. | Contact from object | N.A. | Vegetation | Service Drop | N.A.
107 | PG&E | 2020-02-10 | 13:05 | 40.438 | -122.2828 | Other | Herbaceous | 3 meters - 0.25 Acres | Fire Agency | Anderson FD | Circuit ID:103461101 | Y | 12000 | Pole | Overhead | Y | 2020-02-10 12:59 | 12:59 | Equipment - PG&E | Guy/Span Wire failure | N.A. | N.A. | N.A.
106 | PG&E | 2020-02-10 | 18:51 | 37.0248 | -121.9484 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Fire Agency | Soquel FD | Circuit ID:083252106 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-02-09 10:43 | 18:44 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
336 | PG&E | 2020-02-09 | 11:58 | 38.0545 | -122.2129 | Other | Hardwood Woodland | Structure Only | Fire Agency | Crockett-Carquinez FD | 13432207 | Y | 21000 | Service Drop | Overhead | N | N.A. | N.A. | Under Investigation | N.A. | N.A. | N.A. | N.A. | PG&E has included the following ignition that meets Electric Incident Report criteria, defined by Appendix B to CPUC D.06-04-055. PG&E has not formed a conclusion about the origin or cause of this particular ignition. | EI200209A
1588 | PG&E | 2020-02-09 | 16:34 | 36.8801 | -121.6298 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Agency | Aromas Tri-County Fire Protection District | Circuit ID: 182742104 | Y | 21000 | Conductor - Primary | Overhead | Y | 2020-02-09 | 16:09 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
1829 | PG&E | 2020-02-09 | 15:19 | 38.5468 | -121.742 | Other | Urban | Unknown | Fire Agency | Davis FD | 220741432055 | Y | 12000 | Jumper | Overhead | Y | 2020-02-09 | 14:58 | Equipment - PG&E | Transformer failure | N.A. | N.A. | N.A. | Unknown whether meets reportability threshold, but confirmed to be attributable to PG&E.
102 | PG&E | 2020-02-09 | 10:08 | 39.093 | -120.9634 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Utility - PG&E | N.A. | Circuit ID: 100015965 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-02-09 10:07 | 10:07 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
101 | PG&E | 2020-02-09 | 11:56 | 37.2651 | -119.513 | Vegetation | Barren/Other | 3 meters - 0.25 Acres | Cal Fire | Cal Fire - Rancheria | Circuit ID: 252531103 | Y | 12000 | Conductor - Primary | Overhead | Y | 2020-02-09 06:49 | 6:49 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
100 | PG&E | 2020-02-09 | 16:41 | 37.2528 | -122.0913 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Fire Agency | Santa Clara County FD | 83371107 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-02-09 13:27 | 13:27 | Contact from object | N.A. | Vegetation | Conductor - Primary | N.A.
99 | PG&E | 2020-02-09 | 17:54 | 37.4345 | -122.2163 | Building | Urban | 1 meter - < 3 meters | Unknown | N.A. | Circuit ID: 024251105 | Y | 12000 | Jumper | Overhead | Y | 2020-02-09 | 17:51 | Equipment - PG&E | #N/A | N.A. | N.A. | N.A.
98 | PG&E | 2020-02-09 | 16:25 | 37.6714 | -120.3212 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | N.A. | 252811102 | N | 12000 | Conductor - Primary | Overhead | N | N.A. | N.A. | Equipment - PG&E | Conductor failure-all | N.A. | N.A. | N.A.
86 | PG&E | 2020-02-06 | 13:46 | 39.1216 | -121.1466 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire | N.A. | 152691109 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-02-06 13:35 | 13:35 | Contact from object | N.A. | Animal | Conductor - Primary | N.A.
56 | PG&E | 2020-01-16 | 4:47 | 39.2764 | -122.1631 | Other | Urban | 0.25 - 10 Acres | Fire Agency | Maxwell FD | 62881105 | N | 12000 | Conductor - Primary | Overhead | Y | 2020-01-16 04:42 | 4:42 | Contact from object | N.A. | Vehicle | Conductor - Primary | N.A.