## 2022 Reportables
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations
| Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
SCE | 2022-01-06 | 12:14 | 34.0209 | -118.1503 | Building | Urban | Less Than .25 Acres | Unknown |  | OH-4630520E | AT&T California | 16 | Conductor | Overhead | Yes | 2022-01-06 | 12:14 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-01-09 | 16:10 | 34.1737 | -118.0436 | Building | Urban | Less Than .25 Acres | Fire Agency | Duarte FD | OH-4209491E | Frontier Communications | 4 | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2022-01-12 | 1:10 | 33.8251 | -116.5275 | Vegetation | Urban | Less than three (3) meters of linear travel | Fire Agency | Palm Springs Fire Department | OH-35562S | Frontier Communications | 12 | Conductor | Overhead | Yes | 2022-01-12 | 1:04 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-01-21 | 21:30 | 34.138815 | -117.975658 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1669638E | Frontier Communications | 16 | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Weather
SCE | 2022-01-22 | 10:42 | 34.1102 | -117.6275 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Rancho Cucamonga Fire Department | OH-1205346E | Frontier Communications | 12 | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2022-01-23 | 9:26 | 34.5285 | -117.3341 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Victorville Fire Department | OH-4120760E | None | 12 | Conductor | Overhead | Yes | 2022-01-23 | 7:48 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2022-01-25 | 15:12 | 34.2058 | -118.1952 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1049314E | AT&T California | 16 | Conductor | Overhead | Yes | 2022-01-25 | 14:04 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2022-01-27 | 13:58 | 34.1323 | -118.0018 | Other | Urban | Less Than .25 Acres | Fire Agency | Monrovia Fire Department | OH-1224522E | Frontier Communications | 16 | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2022-01-29 | 10:00 | 34.2632 | -118.8953 | Building | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | UG-5349245 | None | 16 | Conductor | Underground | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2022-02-04 | 10:51 | 34.3151 | -118.8966 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-679512E | AT&T California | 16 | Conductor | Overhead | Yes | 2022-02-04 | 9:35 | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2022-02-04 | 16:15 | 36.3924 | -119.2134 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-723236E | None | 12 | Transformer | Overhead | Yes | 2022-02-04 | 15:47 | Equipment/Facility Failure | Transformer |  |  | Weather
SCE | 2022-02-07 | 8:59 | 35.9352 | -119.2417 | Vegetation | Rural | Less than three (3) meters of linear travel | Unknown |  | OH-4672312E | None | 12 | Conductor | Overhead | Yes | 2022-02-07 | 8:41 | Equipment/Facility Failure | Splice |  |  | Unknown
SCE | 2022-02-11 | 13:19 | 34.1063 | -118.8059 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4216442E | T-Mobile, Verizon Wireless, AT&T Mobility, Corwn Castle NG West, Inc. | 16 | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2022-02-12 | 13:26 | 33.9929 | -118.1265 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-675599H | AT&T California | 16 | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Outside Force
SCE | 2022-02-13 | 10:59 | 33.8089 | -116.4742 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-2032669E | None | 33 | Other | Overhead | Yes | 2022-02-13 | 10:59 | Equipment/Facility Failure | Other |  |  | Other
SCE | 2022-02-14 | 13:08 | 34.1061 | -117.4581 | Building | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-919249E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-02-14 | 13:08 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-02-15 | 20:40 | 34.4036 | -119.4719 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Carpinteria Fire Department | OH-4129624E | None | 16 | Conductor | Overhead | Yes | 2022-02-15 | 21:25 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2022-02-23 | 5:29 | 33.8393 | -117.5935 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-2237511E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-02-23 | 5:29 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2022-03-01 | 13:23 | 33.901063 | -118.310495 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-684895E | AT&T California | 16 | Conductor | Overhead | Yes | 2022-03-01 | 14:28 | Vandalism/Theft | Conductor |  |  | Other
SCE | 2022-03-08 | 14:05 | 33.7354 | -117.9045 | Other | Urban | Less Than .25 Acres | Fire Agency | Santa Ana Fire Department | OH-1550784E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-03-08 | 14:05 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-03-11 | 11:00 | 34.0326 | -118.1372 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Undetermined | OH-1455360E | None | 16 | Conductor | Overhead | Yes | 2022-03-11 | 9:50 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-03-11 | 12:47 | 34.1141 | -117.4046 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-278143E | AT&T California | 12 | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-03-11 | 15:27 | 33.7483 | -116.9499 | Other | Urban | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-1805075E | None | 12 | Conductor | Overhead | Yes | 2022-03-11 | 15:27 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2022-03-12 | 10:51 | 33.925051 | -117.985376 | Other | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-1208365E | Frontier Communications, Time Warner Cable | 12 | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-03-23 | 18:15 | 34.751803 | -118.130804 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Unknown | OH-465397E | Frontier Communications | 12 | Conductor | Overhead | Yes | 2022-03-23 | 16:36 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2022-03-27 | 22:55 | 34.4495 | -119.9004 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1865062E | None | 16 | Conductor | Overhead | Yes | 2022-03-27 | 22:55 | Wire-Wire Contact |  |  |  | Weather
SCE | 2022-03-28 | 18:09 | 35.3324 | -117.6212 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-85057S | None | 33 | Conductor | Overhead | Yes | 2022-03-28 | 16:32 | Equipment/Facility Failure | Insulator |  |  | Weather
SCE | 2022-04-02 | 4:11 | 34.4986 | -117.7454 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-864614E | None | 12 | Conductor | Overhead | Yes | 2022-04-02 | 4:11 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2022-04-08 | 16:41 | 34.3982 | -118.9139 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1908738E | None | 16 | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-04-08 | 19:39 | 33.7861 | -117.9179 | Building | Urban | Less Than .25 Acres | Fire Agency | Orange County FD | OH-4712820E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-04-08 | 19:33 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2022-04-13 | 14:48 | 34.4414 | -119.9234 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Santa Barbara County FD | OH-2144068E | None | 16 | Conductor | Overhead | Yes | 2022-04-13 | 14:48 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2022-04-13 | 18:30 | 34.4634 | -119.9227 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-2178538E | None | 16 | Switch | Overhead | Yes | 2022-04-13 | 17:30 | Equipment/Facility Failure | Switch |  |  | Other
SCE | 2022-04-14 | 12:42 | 36.0947 | -118.9706 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Tulare County Fire Department | OH-2053382E | None | 66 | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2022-04-16 | 14:57 | 34.5901 | -118.2032 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | LACFD | OH-4777414E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-04-16 | 14:57 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-04-22 | 7:04 | 34.0292 | -116.6075 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4507360E | None | 33 | Conductor | Overhead | Yes | 2022-04-22 | 7:04 | Equipment/Facility Failure | Conductor |  |  | Weather
SCE | 2022-04-23 | 10:00 | 33.6362 | -117.8174 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Orange County FD | UG-5081280 | None | 12 | Transformer | Underground | Yes | 2022-04-23 | 9:52 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2022-04-24 | 11:34 | 33.739 | -118.0199 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1370861E | Frontier Communicaitons | 12 | Conductor | Overhead | Yes | 2022-04-24 | 11:34 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-05-05 | 10:31 | 33.842 | -117.5512 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4326229E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-05-05 | 10:31 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2022-05-06 | 20:22 | 33.8576 | -116.5463 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4493823E | None | 33 | Other | Overhead | Yes | 2022-05-06 | 18:22 | Equipment/Facility Failure | Other |  |  | Unknown
SCE | 2022-05-07 | 15:24 | 34.799 | -117.281 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County FD | OH-2285750E | None | 12 | Lightning Arrestor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2022-05-07 | 18:32 | 34.4484 | -119.7407 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Santa Barbara FD | OH-1189031E | Frontier Communications | 4.16 | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2022-05-08 | 14:56 | 34.1119 | -118.1714 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | South Pasadena FD | OH-4808859E | AT&T California, Crown Castle | 16 | Other | Overhead | Yes | 2022-05-08 | 11:33 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2022-05-11 | 12:00 | 36.3889 | -119.2174 | Building | Rural | Less Than .25 Acres | Fire Agency | Tulare City FD | OH-3633T | AT&T California | 12 | Conductor | Overhead | Yes | 2022-05-11 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2022-05-13 | 8:06 | 35.1373 | -117.9626 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4029425E | None | 12 | Conductor | Underground | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2022-05-14 | 11:44 | 35.5045 | -115.434439 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1793829E | None | 33 | Conductor | Overhead | Yes | 2022-05-14 | 11:44 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2022-05-14 | 17:34 | 34.1232 | -117.2456 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County FD | OH-1046452E | Frontier Communications | 4.16 | Conductor | Overhead | Yes | 2022-05-14 | 17:37 | Equipment/Facility Failure | Connector |  |  | Unknown
SCE | 2022-05-16 | 22:42 | 33.8593 | -118.1258 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-841478E | Frontier Communications | 12 | Conductor | Overhead | Yes | 2022-05-16 | 22:42 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2022-05-17 | 11:40 | 34.4823 | -117.205 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Apple Valley Fire Department | OH-2001710E | Frontier Communications | 12 | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error
SCE | 2022-05-18 | 15:27 | 34.0422 | -116.586 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County FD | OH-1685618E | None | 33 | Switch | Overhead | Yes | 2022-05-18 | 15:27 | Normal Operation | Switch |  |  | Human Error
SCE | 2022-05-19 | 14:00 | 35.7148 | -117.8266 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County FD | OH-325400S | Frontier Communications | 12 | Transformer | Overhead | No |  |  | Contact From Object | Transformer | Animal | Electric Facility | Outside Force
SCE | 2022-05-23 | 0:00 | 33.9139 | -118.0125 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1104810E | Frontier Communications | 12 | Conductor | Overhead | Yes | 2022-05-23 | 2:20 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-05-25 | 13:20 | 34.1512 | -119.1183 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Oxnard FD | OH-1581351E | None | 66 | Conductor | Overhead | No |  |  | Contamination |  |  |  | Outside Force
SCE | 2022-05-28 | 1:17 | 34.248 | -116.1462 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1691428E | None | 25 | Conductor | Overhead | Yes | 2022-05-28 | 1:17 | Equipment/Facility Failure | Pole |  |  | Weather
SCE | 2022-05-28 | 10:53 | 34.2031 | -118.8207 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Ventura County FD | OH-1730485E | None | 66 | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Outside Force
SCE | 2022-05-28 | 17:40 | 35.0525 | -118.1897 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1162314E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-05-28 | 16:24 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2022-06-01 | 19:57 | 33.7728 | -116.979 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Hemet FD | OH-2268044E | None | 12 | Switch | Overhead | Yes | 2022-06-01 | 19:57 | Normal Operation | Switch |  |  | Unknown
SCE | 2022-06-02 | 18:46 | 34.1202 | -118.1533 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4667723E | AT&T California | 4.16 | Conductor | Overhead | Yes | 2022-06-02 | 20:45 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2022-06-05 | 5:04 | 35.4771 | -118.9673 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished |  | OH-7023347 | None | 220 | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2022-06-05 | 13:17 | 36.3099 | -119.1352 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-555822E | Frontier Communications | 12 | Conductor | Overhead | Yes | 2022-06-05 | 13:17 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2022-06-06 | 13:06 | 34.6013 | -117.4198 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County FD | OH-4653727E | None | 12 | Conductor | Overhead | Yes | 2022-06-06 | 13:06 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2022-06-07 | 7:57 | 34.5817 | -118.0699 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1161657E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-06-07 | 7:57 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2022-06-07 | 18:23 | 33.9129 | -117.236 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | UG-5152386 | None | 12 | Conductor | Underground | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2022-06-08 | 5:19 | 34.6017 | -118.1266 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4263738E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-06-08 | 5:19 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2022-06-12 | 10:25 | 34.0543 | -118.1517 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-1244558E | None | 16 | Lightning Arrestor | Overhead | Yes | 2022-06-12 | 10:24 | Contact From Object | Lightning Arrestor | Animal | Electric Facility | Outside Force
SCE | 2022-06-13 | 9:00 | 33.857984 | -118.252869 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-2239674E | AT&T California | 16 | Conductor | Overhead | Yes | 2022-06-13 | 8:42 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2022-06-16 | 12:38 | 34.665393 | -118.288833 | Vegetation | Urban | 10 - 99 Acres | Fire Agency | LACFD | OH-4756547E, OH-4244499E | None | 12 | Conductor | Overhead | Yes | 2022-06-16 | 12:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-06-17 | 16:13 | 34.4165 | -119.5196 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Santa Barbara County FD, Carpinteria FD, CAL FIRE | OH-1217781E | Frontier Communications | 16 | Transformer | Overhead | Yes | 2022-06-17 | 19:36 | Equipment/Facility Failure | Transformer |  |  | Unknown
SCE | 2022-06-18 | 0:03 | 34.0901 | -118.6026 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | UG-5641017 | None | 16 | Transformer | Underground | Yes | 2022-06-17 | 20:11 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2022-06-21 | 5:10 | 34.0356 | -118.0906 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Montebello FD | OH-7028424 | None | 500 | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Unknown
SCE | 2022-06-21 | 14:04 | 34.0419 | -117.2845 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Unknown | OH-4346458E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-06-21 | 15:57 | Equipment/Facility Failure | Tap |  |  | Unknown
SCE | 2022-06-22 | 23:00 | 34.8946 | -116.6748 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-2268549E | None | 12 | Other | Overhead | Yes | 2022-06-22 | 22:09 | Other | Pole |  |  | Weather
SCE | 2022-06-22 | 23:37 | 34.3839 | -118.5561 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Valencia FD | UG-5036043 | None | 16 | Conductor | Underground | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2022-06-24 | 1:05 | 34.0986 | -118.1003 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1551552E | None | 66 | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Weather
SCE | 2022-06-24 | 15:20 | 34.1882 | -118.8708 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County FD | OH-1473508E | Frontier Communications & AT&T California | 16 | Switch | Overhead | Yes | 2022-06-24 | 15:07 | Equipment/Facility Failure | Switch |  |  | Human Error
SCE | 2022-06-24 | 20:34 | 34.3938 | -118.6996 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | LACFD & Ventura County FD | OH-7020111 | None | 66 | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2022-06-27 | 15:45 | 33.9962 | -118.1338 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1152478E | None | 16 | Transformer | Overhead | Yes | 2022-06-27 | 15:35 | Equipment/Facility Failure | Transformer |  |  | Unknown
SCE | 2022-06-28 | 19:16 | 34.0407 | -118.6974 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Malibu FD | OH-4744779E | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Switch | Overhead | Yes | 2022-06-28 | 19:16 | Equipment/Facility Failure | Switch |  |  | Other
SCE | 2022-07-04 | 18:35 | 33.9036 | -117.9141 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Brea FD, Fullerton FD | OH-1440534E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-07-04 | 18:34 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-07-08 | 22:45 | 34.4746 | -118.608 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | LACFD | OH-7022813 | None | 220 | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2022-07-10 | 11:22 | 34.5715 | -117.934 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1062114E | None | 12 | Conductor | Overhead | Yes | 2022-07-10 | 11:22 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2022-07-10 | 19:53 | 34.2443 | -118.8293 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4216505E | AT&T California | 16 | Conductor | Overhead | Yes | 2022-07-10 | 19:53 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2022-07-13 | 7:07 | 33.6858 | -117.9549 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | UG-5107647 | None | 12 | Transformer | Underground | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2022-07-14 | 16:53 | 33.9173 | -118.2534 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Unknown | OH-4292421E | AT&T California | 16 | Switch | Overhead | Yes | 2022-07-14 | 16:53 | Equipment/Facility Failure | Switch |  |  | Unknown
SCE | 2022-07-16 | 18:37 | 33.9368 | -117.9279 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1124329E | Frontier Communications | 12 | Conductor | Overhead | Yes | 2022-07-16 | 16:20 | Contact from Object | Conductor | Balloons | Electric Facility | Outside Force
SCE | 2022-07-17 | 18:30 | 33.8014 | -116.5468 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Palm Springs Fire Department | OH-235349S | None | 4.16 | Other | Underground | Yes | 2022-07-17 | 21:53 | Equipment/Facility Failure | Other |  |  | Unknown
SCE | 2022-07-18 | 17:02 | 34.0052 | -117.5887 | Structure | Urban | Less Than .25 Acres | Unknown |  | UG-5443474 | None | 12 | Conductor | Underground | No |  |  | Equipment/Facility Failure | Other |  |  | Unknown
SCE | 2022-07-26 | 10:45 | 34.6604 | -118.2023 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4170477E | None | 12 | Lightning Arrestor | Overhead | Yes | 2022-07-26 | 5:58 | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown
SCE | 2022-07-29 | 18:03 | 34.454 | -119.2322 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | UG-5035181 | None | 16 | Conductor | Underground | No |  |  | Equipment/Facility Failure | Connector |  |  | Unknown
SCE | 2022-07-29 | 22:37 | 34.0738 | -117.1923 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4612709E | None | 12 | Conductor | Overhead | Yes | 2022-07-29 | 22:37 | Contact From Object | Conductor | Vehicle | Pole | Outside Force
SCE | 2022-08-07 | 12:00 | 34.2845 | -118.713 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-3002750E | AT&T California | 16 | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2022-08-09 | 19:07 | 34.2177 | -119.0058 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County FD | OH-1662405E | None | 16 | Other | Overhead | Yes | 2022-08-09 | 17:59 | Equipment/Facility Failure | Connector |  |  | Unknown
SCE | 2022-08-09 | 19:41 | 33.9804 | -117.9034 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-1457241E | Frontier Communications | 12 | Conductor | Overhead | No |  |  | Contact From Object | Conductor | Vegetation | Electric Facility | Outside Force
SCE | 2022-08-11 | 4:09 | 34.0267 | -117.3147 | Structure | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County FD | OH-2007004E | AT&T California | 12 | Capacitor Bank | Overhead | No |  |  | Equipment/Facility Failure | Capacitor Bank |  |  | Other
SCE | 2022-08-11 | 10:38 | 34.1348 | -117.8796 | Structure | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-664282E | Frontier California | 12 | Conductor | Overhead | Yes | 2022-08-11 | 10:38 | Contact From Object | Conductor | Vegetation | Electric Facility | Outside Force
SCE | 2022-08-14 | 3:53 | 34.0879 | -117.3886 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | UG-5162399 | None | 12 | Conductor | Underground | Yes | 2022-08-14 | 3:01 | Equipment/Facility Failure | Connector |  |  | Unknown
SCE | 2022-08-18 | 11:53 | 35.8775 | -119.2445 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County FD | OH-401486E | AT&T California | 12 | Conductor | Overhead | Yes | 2022-08-18 | 11:53 | Contact From Object | Conductor | Vehicle | Pole | Outside Force
SCE | 2022-08-19 | 15:31 | 34.7752 | -118.4231 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | OH-1312410E | None | 66 | Conductor | Overhead | No |  |  | Contact From Object | Conductor | Vehicle | Pole | Outside Force
SCE | 2022-08-19 | 18:50 | 34.287 | -118.3739 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4859719E | None | 16 | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2022-08-24 | 15:33 | 34.313 | -119.1857 | Vegetation | Rural | Less Than .25 Acres | Customer |  | OH-7020188 | None | 66 | Other | Overhead | No |  |  | Contact From Object | Splice/Clamp/Connector | Animal | Electric Facility | Outside Force
SCE | 2022-08-28 | 18:49 | 36.0115 | -119.4111 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County FD | OH-4639497E | AT&T California | 12 | Transformer | Overhead | Yes | 2022-08-28 | 18:49 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2022-08-31 | 16:39 | 34.0666 | -118.1038 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1723355E | AT&T California | 16 | Capacitor Bank | Overhead | Yes | 2022-08-31 | 13:27 | Equipment/Facility Failure | Capacitor Bank |  |  | Unknown
SCE | 2022-09-01 | 14:00 | 34.159535 | -118.732375 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Local FD | OH-4835986E | AT&T California | 16 | Conductor | Overhead | Yes | 2022-09-01 | 14:00 | Equipment/Facility Failure | Conductor |  |  | Weather
SCE | 2022-09-03 | 15:29 | 34.7192 | -118.0124 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LACFD | OH-538399E | Frontier Communications | 12 | Conductor | Overhead | Yes | 2022-09-03 | 13:08 | Contact From Object | Conductor | Vehicle | Pole | Outside Force
SCE | 2022-09-04 | 13:00 | 34.214 | -118.8433 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County FD | UG-5025657 | None | 16 | Transformer | Underground | No |  |  | Equipment/Facility Failure | Transformer |  |  | Weather
SCE | 2022-09-05 | 16:50 | 33.6229 | -117.6177 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | UG-5398427 | None | 12 | Transformer | Underground | No |  |  | Equipment/Facility Failure | Transformer |  |  | Unknown
SCE | 2022-09-06 | 8:16 | 35.308794 | -117.951397 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1899893E | None | 12 | Other | Overhead | Yes | 2022-09-06 | 11:35 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2022-09-06 | 19:23 | 34.7744 | -118.768 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | OH-4053152E | None | 12 | Conductor | Overhead | Yes | 2022-09-06 | 19:23 | Unknown |  | Unknown | Electric Facility | Unknown
SCE | 2022-09-08 | 16:32 | 35.6215 | -119.0393 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Kern County FD | OH-7022622 | None | 220 | Conductor | Overhead | No |  |  | Contact From Object | Insulator | Animal | Electric Facility | Outside Force
SCE | 2022-09-09 | 17:46 | 35.8709 | -118.6384 | Vegetation | Rural | Less Than .25 Acres | Customer |  | OH-4354609E | None | 2.4 | Fuse | Overhead | Yes | 2022-09-09 | 17:46 | Equipment/Facility Failure | Fuse |  |  | Unknown
SCE | 2022-09-27 | 14:49 | 34.0641 | -117.3891 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County FD | UG-5456683 | None | 12 | Transformer | Underground | Yes | 2022-09-27 | 13:51 | Vandalism/Theft | Transformer |  |  | Other
SCE | 2022-09-28 | 15:39 | 34.452 | -119.2342 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ventura County FD | OH-4413379E | AT&T California | 16 | Conductor | Overhead | Yes | 2022-09-28 | 15:30 | Contact From Object | Conductor | Vegetation | Electric Facility | Outside Force
SCE | 2022-09-29 | 14:46 | 35.6027 | -119.0361 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-7022631 | None | 220 | Conductor | Overhead | No |  |  | Contact From Object | Conductor | Animal | Electric Facility | Outside Force
SCE | 2022-10-02 | 15:27 | 34.447854 | -119.857387 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Santa Barbara County FD | OH-1524340E | None | 16 | Conductor | Overhead | Yes | 2022-10-02 | 16:09 | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | 2022-10-09 | 17:38 | 34.5809 | -118.1203 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1805355E | None | 12 | Conductor | Overhead | Yes | 2022-10-09 | 17:38 | Contact From Object | Conductor | Vehicle | Electric Facility | Outside Force
SCE | 2022-10-10 | 22:43 | 34.0748 | -117.2685 | Vegetation | Urban | Less Than .25 Acres | Utility |  | UG-5345492 | None | 12 | Transformer | Padmount | Yes | 2022-10-10 | 20:06 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2022-10-24 | 21:07 | 34.3338 | -119.385 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | OH-4375257E | None | 16 | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Connector |  |  | Unknown
SCE | 2022-10-30 | 3:38 | 33.605 | -114.7206 | Structure | Rural | Less Than .25 Acres | Unknown |  | OH-4259458E | Frontier Communications | 12 | Other | Underground | Yes | 2022-10-30 | 3:36 | Unknown | Secondary Riser |  |  | Unknown
SCE | 2022-11-02 | 1:07 | 34.2184 | -119.0652 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura City FD | OH-1270470E | None | 16 | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Weather
SCE | 2022-11-02 | 9:04 | 33.848 | -118.0104 | Building | Urban | Less Than .25 Acres | Unknown |  | OH-1291924E | AT&T California | 12 | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Weather
SCE | 2022-11-04 | 12:37 | 33.7746 | -117.8803 | Structure | Urban | Less Than .25 Acres | Unknown |  | UG-5309451 | None | 12 | Transformer | Padmount | Yes | 2022-11-04 | 11:00 | Equipment/Facility Failure | Transformer |  |  | Unknown
SCE | 2022-11-16 | 10:00 | 34.0966 | -118.5992 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | LACFD | OH-3006767E | Frontier Communications | 16 | Conductor | Overhead | Yes | 2022-11-16 | 10:00 | Contact From Object | Pole | Vegetation | Electric Facility | Weather
SCE | 2022-11-21 | 22:30 | 33.983 | -118.1269 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-2108709E | Verizon Wireless & AT&T California | 16 | Conductor | Underground | Yes | 2022-11-21 | 22:33 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2022-11-23 | 22:29 | 33.858 | -117.4333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL Fire | OH-1670371E | None | 12 | Conductor | Overhead | Yes | 2022-11-23 | 22:29 | Contact From Object | Conductor | Vegetation | Electric Facility | Weather
SCE | 2022-11-27 | 8:39 | 34.0976 | -117.8246 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Local FD | OH-1489533E | Frontier Communications | 12 | Conductor | Overhead | Yes | 2022-11-27 | 8:39 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2022-11-29 | 3:32 | 35.6 | -117.7032 | Structure | Rural | Less Than .25 Acres | Fire Agency | Kern County FD | OH-2025102E | Frontier Communications | 12 | Conductor | Underground | No |  |  | Vandalism/Theft | Conductor |  |  | Outside Force
SCE | 2022-12-26 | 11:17 | 33.7069 | -117.179 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | UG-5516998 | None | 12 | Transformer | Padmount | Yes | 2022-12-26 | 10:47 | Contact From Object | Transformer | Vehicle | Electric Facility | Outside Force
Note on B2: Date the event started (Use MM/DD/YY when inputting dates)
Note on C2: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on D2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on E2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on F2: Material involved in the initial fueling of the fire;
Note on G2: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on H2: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on I2: Is who suppressed the fire
Note on K2: Utility’s description of the pole and/or equipment involved.
Note on L2: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on M2: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on N2: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on O2: The equipment involved in the event (overhead, padmounted or subsurface);
Note on P2: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on Q2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on R2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on S2: The suspected cause of the ignition;
Note on T2: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on U2: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on V2: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on W2: Factors that contributed to the ignition;
Note on S75: A cessation of normal operation
Note on S90: A cessation of normal operation
Note on S93: A cessation of normal operation
Note on S95: A cessation of normal operation
Note on S101: A cessation of normal operation