## Interactive (2021)
Utility Name |  |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Suspected Cause
| Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Ignition Cause | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
SDG&E | 2021-02-28 | 14:00 | 33.437 | -117.569 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | P227391 |  | 12kv | Transformer | Overhead | Yes | 2021-02-28 | 14:00 | Contact From Object |  | Animal | Electric Facility | Outside Force
SDG&E | 2021-03-22 | 8:00 | 33.2431 | -117.3598 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | Z222386 |  | 230kV | Conductor | Overhead | No |  |  | Contact From Object | Conductor | Balloons |  | Other
SDG&E | 2021-03-25 | 10:00 | 32.971 | -117.262 | Vegetation | Urban | Less Than .25 Acres | Utility |  | Z12304 |  | 12kv | Transformer | Overhead | Yes | 2021-03-25 | 10:00 | Equipment/Facility Failure | Transformer |  |  | Unknown
SDG&E | 2021-04-30 | 13:55 | 33.0178 | -116.8661 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ramona CAL FIRE | P110643 |  | 120v | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SDG&E | 2021-05-07 | 13:10 | 33.338 | -117.154 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE/ NCFPD |  |  | 12kv | Conductor | Overhead | Yes | 2021-05-07 | 13:10 | Unknown |  | Other | Electric Facility | Outside Force
SDG&E | 2021-05-11 | 10:48 | 32.85 | -116.936 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Lakeside FD |  |  | 12kv | Conductor | Overhead | Yes | 2021-05-11 | 10:48 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SDG&E | 2021-05-19 | 11:00 | 32.834 | -117.1834 | Vegetation | Urban | Less Than .25 Acres | Utility |  | Z92509 |  | 12kv | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Human Error
SDG&E | 2021-05-24 | 13:40 | 32.742 | -117.145 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Diego FD | P2107172488 |  | 120v | Conductor | Overhead | Yes | 2021-05-24 | 13:40 | Contact From Object |  | Vegetation | Electric Facility | None
SDG&E | 2021-06-13 | 12:00 | 33.0265 | -116.858 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ramona CAL FIRE | P107449 |  | 12kv | Conductor | Overhead | Yes | 2021-06-13 | 12:00 | Contact From Object |  | Balloons | Electric Facility | Other
SDG&E | 2021-06-16 | 14:27 | 33.3483 | -116.7324 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P239535 |  | 12kv | Switch | Overhead | Yes | 2021-06-16 | 14:27 | Equipment/Facility Failure | Switch |  |  | Unknown
SDG&E | 2021-06-17 | 9:51 | 32.6037 | -116.6113 | Vegetation | Rural | Less Than .25 Acres | Utility |  | P176917 |  | 12kV | Conductor | Overhead | Yes | 2021-06-17 | 9:52 | Equipment/Facility Failure | Conductor |  |  | Unknown
SDG&E | 2021-06-18 | 10:51 | 33.1462 | -117.0478 | Other | Urban | Less Than .25 Acres | Fire Agency | Escondido | Z314050, 456-23CW, C456 | telco | 12kV | Capacitor Bank | Overhead | Yes | 2021-06-18 | 10:51 | Equipment/Facility Failure | Capacitor Bank |  |  | None
SDG&E | 2021-07-01 | 7:42 | 33.2806 | -117.1574 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE/ NCFPD | P119250 |  | 12kV | Conductor | Overhead | Yes | 2021-07-01 | 7:42 | Vandalism/Theft | Conductor |  |  | Outside Force
SDG&E | 2021-07-14 | 18:26 | 32.5038 | -116.5553 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished |  | 372756J |  | 12kv | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SDG&E | 2021-07-18 | 6:18 | 33.262 | -117.429 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | Z21137 |  | 12kv | Other | Overhead | No |  |  | Other |  |  |  | Weather
SDG&E | 2021-07-24 | 15:19 | 32.7058 | -116.7315 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FiRE/ USFS | P74739 |  | 12kv | Other | Overhead | Yes | 2021-07-24 | 15:19 | Contact From Object |  | Animal | Electric Facility | Outside Force
SDG&E | 2021-07-28 | 13:51 | 33.2282 | -116.983 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Z16445 |  | 12kv | Conductor | Overhead | Yes | 2021-07-28 | 13:51 | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Human Error
SDG&E | 2021-07-29 | 18:31 | 33.0993 | -117.0662 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Escondido | P511401 |  | 240v | Conductor | Overhead | Yes | 2021-07-29 | 18:31 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SDG&E | 2021-08-06 | 14:00 | 32.716 | -116.814 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL Fire | P278802 |  | 240v | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Weather
SDG&E | 2021-08-07 | 11:00 | 32.824 | -116.913 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Lakeside FD | P73808 |  | 12kv | Conductor | Overhead | Yes | 2021-08-07 | 11:08 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SDG&E | 2021-08-25 | 5:25 | 33.0827 | -116.9698 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Diego FD | P11679 |  | 12kv | Conductor | Overhead | Yes | 2021-08-25 | 5:25 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SDG&E | 2021-10-01 | 0:00 | 32.6923 | -116.9605 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FWS | Z971845 |  | 230kV | Other | Overhead | Yes | 2021-10-01 | 1202 | Contact From Object |  | Balloons | Electric Facility | Unknown
SDG&E | 2021-11-30 | 9:46 | 32.8561 | -116.9605 | Vegetation | Urban | Less Than .25 Acres | Customer |  | Z173078 |  | 12kv | Switch | Overhead | Yes | 2021-11-30 | 9:46 | Contact From Object |  | Animal | Electric Facility | Outside Force
SDG&E | 2021-12-03 | 12:20 | 32.568 | -116.962 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Diego FD | P226534 |  | 12kv | Switch | Overhead | Yes | 2021-12-03 | 1048.5139 | Contact From Object |  | Animal | Electric Facility | Outside Force
SDG&E | 2021-12-06 | 14:13 | 32.6762 | -116.7286 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL FIRE | P372261 |  | 12kV | Other | Overhead | Yes | 2021-12-06 | 14:13 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
Note on A1: Name of utility reporting the event
Note on B2: Date the event started (Use MM/DD/YY when inputting dates)
Note on C2: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on D2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on E2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on F2: Material involved in the initial fueling of the fire;
Note on G2: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on H2: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on I2: Is who suppressed the fire
Note on J2: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on K2: Utility’s description of the pole and/or equipment involved.
Note on L2: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on M2: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on N2: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on O2: The equipment involved in the event (overhead, padmounted or subsurface);
Note on P2: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on Q2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on R2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on S2: The suspected cause of the ignition;
Note on T2: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on U2: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on V2: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on W2: Factors that contributed to the ignition;

## Drop Downs (hidden)
BVES | Building | Rural | Customer | Capacitor Bank | Padmounted | Contact Between Third Party Facility on Pole and Supply Lines | Animal | Human Error | Yes | Less Than .25 Acres | Communication Facility | Capacitor Bank | Transmission | EA | Normal | January | 1 | WM
Kirkwood Meadows | Other | Urban | Fire Agency | Conductor | Overhead | Contact From Object | Balloons | None | No | .26 - 9.99 Acres | Electric Facility | Conductor | Distribution | ME | Elevated | February | 2 | DP
Liberty Energy | Vegetation |  | Self Extinguished | Fuse | Subsurface | Contamination | Other | Other |  | 10 - 99 Acres | Pole | Fuse | Secondary | NE | Extreme | March | 3 | DB
PacifiCorp |  |  | Unknown | Lightning Arrestor |  | Equipment/Facility Failure | Vegetation | Outside Force |  | 100 - 299 Acres |  | Insulator |  | RA |  | April | 4 | MR
PG&E |  |  | Utility | Other |  | Normal Operation | Vehicle | Unknown |  | 3000 - 999 Acres |  | Lightning Arrestor |  | CM |  | May | 5 | SP
SCE |  |  |  | Switch |  | Other |  | Weather |  | 1000 - 4999 Acres |  | Pole |  | BC |  | June | 6 | RV
SDG&E |  |  |  | Transformer |  | Unknown |  |  |  | Greater than 5000 Acres |  | Guy/Span Wire |  | NC |  | July | 7
[6 empty] | Vandalism/Theft |  |  |  | Less than three (3) meters of linear travel |  | Other |  | OC |  | August | 8
[6 empty] | Wire-Wire Contact |  |  |  | Structure Only |  | Protective Relay |  |  |  | September | 9
[12 empty] | Crossarm |  |  |  | October | 10
[12 empty] | Recloser |  |  |  | November | 11
[12 empty] | Sectionalizer |  |  |  | December | 12
[12 empty] | Splice/Clamp/Connector |  |  |  |  | 13
[12 empty] | Switch |  |  |  |  | 14
[12 empty] | Transformer |  |  |  |  | 15
[12 empty] | Voltage Regulator |  |  |  |  | 16
17
Note on G2: To be used when contact between a supply facility and non-supply facility on a pole occurred. Note: This field does not specify which facility caused the contact, only that the contact occurred.
Note on G3: Use when contact from outside object caused the incidnet.
Note on G4: Should be used when outside contaminates effect the utility's facilities. Examples: Smoke caused a phase to phase arc which resulted in a fire. Dirt and salt allowed tracking on an insulator, which caused a crossarm to catch on fire and then resulted in a vegetation fire.
Note on G5: A cessation of normal operation
Note on G6: To be used when the supply facility operated normally. Example: A fuse operated and material fell onto vegetation and started a fire.
Note on G9: This field would include those fires started from gunshots that broke electric equipment, attempted theft of copper cable, etc.
Note on G10: To be used when to two or more supply conductors contact each other.